## Read_me
Drawing package | Main duct and return / 11 method sheets + 3 scaled reference plans / 85 retained instruments + 22 new DX candidates
Architecture | DX PAU bank -> roof common SA main -> nine room drops; six room returns -> roof common RA main -> bank. Dedicated extracts separate.
Main location | User selected ROOF COMMON MAINS WITH ROOM DROPS. Scaled roof plan is a floor-footprint proposal; roof survey and OEM approval pending.
Ceiling | User slab U/S4000, ceiling3300 mm. Indoor room depth <=400 mm, BOD3400. Roof SA BOD4800, RA5550 proposed; 50 indoor/75 outdoor insulation assumptions.
Scope | Method drawings / sizing only; actual building routing, supports, structure, fan ESP, DX capacity and OEM selections pending.
AutoCAD | Open Main duct and return.dxf; MDR01_A1 through MDR14_A1; Save As DWG. Native AutoCAD plotting has not run.
Input editing | Original inputs retained; edit build.py for the method assumptions. Generated workbook edits are not imported.

## Retained_instruments
tag | parameter | location | io | basis | provision | action
TT-GF-02 | Dry bulb temperature | GF-02 Electrical panel | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-02 | Relative humidity | GF-02 Electrical panel | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-02 | Room pressure vs outdoor | GF-02 Electrical panel | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-04 | Dry bulb temperature | GF-04 Meeting | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-04 | Relative humidity | GF-04 Meeting | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-04 | Room pressure vs outdoor | GF-04 Meeting | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-04 | Heater high temperature limit | EH-04 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-08 | Dry bulb temperature | GF-08 Telecom panel | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-08 | Relative humidity | GF-08 Telecom panel | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-08 | Room pressure vs outdoor | GF-08 Telecom panel | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-05 | Dry bulb temperature | GF-05 Operator console | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-05 | Relative humidity | GF-05 Operator console | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-05 | Room pressure vs outdoor | GF-05 Operator console | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-05 | Heater high temperature limit | EH-05 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-06 | Dry bulb temperature | GF-06 Reception / corridor | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-06 | Relative humidity | GF-06 Reception / corridor | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-06 | Room pressure vs outdoor | GF-06 Reception / corridor | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Required | Monitor / alarm; final range and limits TBC
TSHH-EH-06 | Heater high temperature limit | EH-06 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-09 | Dry bulb temperature | GF-09 Toilet group: two cubicles | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-09 | Relative humidity | GF-09 Toilet group: two cubicles | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-09 | Room pressure vs outdoor | GF-09 Toilet group: two cubicles | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-07 | Dry bulb temperature | GF-07 Bedroom / Resting Room | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-07 | Relative humidity | GF-07 Bedroom / Resting Room | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-07 | Room pressure vs outdoor | GF-07 Bedroom / Resting Room | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-07 | Heater high temperature limit | EH-07 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-03 | Dry bulb temperature | GF-03 Kitchen / kitchenette | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-03 | Relative humidity | GF-03 Kitchen / kitchenette | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-03 | Room pressure vs outdoor | GF-03 Kitchen / kitchenette | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-03 | Heater high temperature limit | EH-03 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-01 | Dry bulb temperature | GF-01 Clean-agent cylinder room | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-01 | Relative humidity | GF-01 Clean-agent cylinder room | AI | 8.4.1 humidity provision | Additional proposal | Monitor / alarm; final range and limits TBC
DPT-GF-01 | Room pressure vs outdoor | GF-01 Clean-agent cylinder room | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-SA-01 | Supply air temperature | Common supply | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
TT-RA-01 | Return air temperature | Common return | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
RHT-RA-01 | Return relative humidity | Common return | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
FIT-SA-01 | Common supply airflow | Common supply straight length per manufacturer | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
FIT-RA-01 | Common return airflow | Common return straight length per manufacturer | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
PDT-OA-01 | Outdoor intake filter differential pressure | F-OA-01 | AI | Additional intake filter monitoring | Additional proposal | Monitor / alarm; final range and limits TBC
PDI-OA-01 | Local intake filter differential pressure gauge | F-OA-01 | LOCAL | Additional intake filter monitoring | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-COM-01 | Common heater high-limit | EH-COM-01 | DI | Proposed OEM heater safety | OEM safety provision | Trip common heater; reset per OEM
PDT-F1-A | Filter differential pressure | PAU-A filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-A | Local filter differential pressure gauge | PAU-A filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-A | Filter differential pressure | PAU-A filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-A | Local filter differential pressure gauge | PAU-A filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-A | Evaporator fan differential pressure | PAU-A fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-A | RMS vibration velocity | PAU-A frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
PDT-F1-B | Filter differential pressure | PAU-B filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-B | Local filter differential pressure gauge | PAU-B filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-B | Filter differential pressure | PAU-B filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-B | Local filter differential pressure gauge | PAU-B filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-B | Evaporator fan differential pressure | PAU-B fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-B | RMS vibration velocity | PAU-B frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
PDT-F1-C | Filter differential pressure | PAU-C filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-C | Local filter differential pressure gauge | PAU-C filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-C | Filter differential pressure | PAU-C filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-C | Local filter differential pressure gauge | PAU-C filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-C | Evaporator fan differential pressure | PAU-C fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-C | RMS vibration velocity | PAU-C frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-03-01 | Extract fan pressure proof | EF-03-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-03-01 | RMS vibration velocity | EF-03-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-03-02 | Extract fan pressure proof | EF-03-02 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-03-02 | RMS vibration velocity | EF-03-02 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-09-01 | Extract fan pressure proof | EF-09-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-09-01 | RMS vibration velocity | EF-09-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-09-02 | Extract fan pressure proof | EF-09-02 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-09-02 | RMS vibration velocity | EF-09-02 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-01-01 | Extract fan pressure proof | EF-01-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-01-01 | RMS vibration velocity | EF-01-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-SF-B1-01 | Fan pressure proof | SF-B1-01 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-SF-B1-01 | RMS vibration velocity | SF-B1-01 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-SF-B1-02 | Fan pressure proof | SF-B1-02 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-SF-B1-02 | RMS vibration velocity | SF-B1-02 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-EF-B1-01 | Fan pressure proof | EF-B1-01 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-EF-B1-01 | RMS vibration velocity | EF-B1-01 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-EF-B1-02 | Fan pressure proof | EF-B1-02 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-EF-B1-02 | RMS vibration velocity | EF-B1-02 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
TT-B1-01 | Cable basement air temperature | Cable basement | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-B1-01 | Basement pressure vs outdoor | Cable basement | AI | Additional coordination provision | Additional proposal | Monitor / alarm; final range and limits TBC
EM-HPCP-01 | Energy metering: V, I, kW, kWh, PF, Hz; THD for VFD | HPCP feeders >7.5 kW | COMM | 8.4.1 | Required where threshold met | Power ratings / feeder quantity / protocol TBC
AFS-EH-04 | Airflow proving switch for heater safety permissive | Electric heater EH-04 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-05 | Airflow proving switch for heater safety permissive | Electric heater EH-05 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-06 | Airflow proving switch for heater safety permissive | Electric heater EH-06 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-07 | Airflow proving switch for heater safety permissive | Electric heater EH-07 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-03 | Airflow proving switch for heater safety permissive | Electric heater EH-03 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-COM-01 | Airflow proving switch for heater safety permissive | Electric heater EH-COM-01 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active

## Retained_IO
tag | type | signal | action | basis | status
TT-GF-02 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-02 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-02 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-04 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-04 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-04 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-04 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-08 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-08 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-08 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-05 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-05 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-05 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-05 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-06 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-06 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-06 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-06 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-09 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-09 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-09 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-07 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-07 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-07 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-07 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-03 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-03 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-03 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-03 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-01 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-01 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-01 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-SA-01 | AI | Supply air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
TT-RA-01 | AI | Return air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
RHT-RA-01 | AI | Return relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
FIT-SA-01 | AI | Common supply airflow | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
FIT-RA-01 | AI | Common return airflow | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
PDT-OA-01 | AI | Outdoor intake filter differential pressure | Monitor / alarm; final range and limits TBC | Additional intake filter monitoring | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-COM-01 | DI | Common heater high-limit | Trip common heater; reset per OEM | Proposed OEM heater safety | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-A | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-A | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-A | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-A | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-B | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-B | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-B | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-C | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-C | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-C | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-C | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-03-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-03-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-03-02 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-03-02 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-09-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-09-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-09-02 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-09-02 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-01-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-01-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B1-01 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-SF-B1-01 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B1-02 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-SF-B1-02 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-B1-01 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-EF-B1-01 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-B1-02 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-EF-B1-02 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
TT-B1-01 | AI | Cable basement air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-B1-01 | AI | Basement pressure vs outdoor | Monitor / alarm; final range and limits TBC | Additional coordination provision | Draft point allocation; safety integrity / module allocation TBC
EM-HPCP-01 | COMM | Energy metering: V, I, kW, kWh, PF, Hz; THD for VFD | Power ratings / feeder quantity / protocol TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
EH-04-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-04-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-05-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-05-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-06-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-06-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-07-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-07-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-03-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-03-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-COM-01-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-COM-01-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
FACP-FIRE-01 | DI | Confirmed fire from FACP | Stop entire HVAC; latch fire ESD | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
HPCP-ESTOP-01 | DI | Panel emergency stop | Stop / isolate per approved ESD | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
RESET-01 | DI | Local manual reset | Only after fire signal / fault clears | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
BMS-START-01 | COMM | Initial start | Normal permissives apply | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
BMS-ESD-01 | COMM | Remote emergency stop | Stop HVAC; approved mapping TBC | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
AFS-EH-04 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-05 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-06 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-07 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-03 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-COM-01 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending

## All_terminals
tag | room | air_type | flow_l_s | neck_dia_mm | face_w_mm | face_h_mm | x_mm | y_mm | level | catalogue
SD-02-01 | 02 | SA | 166.2 | 350 | 600 | 600 | 2700 | 17700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-02 | 02 | SA | 166.2 | 350 | 600 | 600 | 7100 | 17700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-03 | 02 | SA | 166.2 | 350 | 600 | 600 | 2700 | 13100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-04 | 02 | SA | 166.2 | 350 | 600 | 600 | 7100 | 13100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-02-01 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 2000 | 17000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-02 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 7700 | 17000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-03 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 2000 | 11900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-04 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 7700 | 11900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-04-01 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 1800 | 6600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-04-02 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 4100 | 4300 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-04-03 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 1900 | 1900 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-04-01 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 700 | 7200 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-04-02 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 5000 | 4300 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-04-03 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 700 | 1000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-08-01 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6800 | 6500 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-02 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 6500 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-03 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6800 | 4200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-04 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 4200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-05 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6800 | 1700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-06 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 1700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-08-01 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5500 | 7150 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-02 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11400 | 7150 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-03 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5500 | 4600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-04 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11400 | 4600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-05 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5500 | 900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-06 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11400 | 900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-05-01 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 10900 | 18100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-02 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 16600 | 18100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-03 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 18300 | 15800 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-04 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 10900 | 13600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-05 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 16600 | 13600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-05-01 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 9900 | 18800 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-02 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 19000 | 18800 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-03 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 9900 | 14600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-04 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 19000 | 12500 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-05 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 15100 | 12000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-06-01 | 06 | SA | 139.4 | 300 | 600 | 600 | 5400 | 10150 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-06-02 | 06 | SA | 139.4 | 300 | 600 | 600 | 14700 | 10150 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-06-03 | 06 | SA | 139.4 | 300 | 600 | 600 | 18300 | 10150 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-06-01 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 4500 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-02 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 9700 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-03 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 17200 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-04 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 18300 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-09-01 | 09 | SA | 23.1 | 150 | 300 | 300 | 13600 | 7000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-09-02 | 09 | SA | 23.1 | 150 | 300 | 300 | 13600 | 5200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-07-01 | 07 | SA | 168.2 | 350 | 600 | 600 | 13900 | 3200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-07-01 | 07 | RA | 108.863389603607 | 300 | 500 | 500 | 14400 | 1400 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-03-01 | 03 | SA | 147.6 | 325 | 600 | 600 | 18600 | 6600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-01-01 | 01 | SA | 141.3 | 300 | 600 | 600 | 18100 | 3000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
EG-09-01 | 09 | EA | 32.44444444444444 | 150 | 300 | 300 | 14200 | 7000 | Pickup height TBC | TBC
EG-09-02 | 09 | EA | 32.44444444444444 | 150 | 300 | 300 | 14200 | 5200 | Pickup height TBC | TBC
EG-03-01 | 03 | EA | 147.6 | 300 | 500 | 500 | 18900 | 5700 | Pickup height TBC | TBC
EG-01-01 | 01 | EA | TBC | TBC | 500 | 500 | 18600 | 1500 | Pickup height TBC | TBC

## Retained_components
tag | service | basis | selection_status
VCD-S02 | Supply branch balancing damper | Room GF-02 | Proposed; OEM selection TBC
FSD-S02 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-02-01 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-02 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-03 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-04 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
RCD-R02 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R02 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-02-01 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-02 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-03 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-04 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
VCD-S04 | Supply branch balancing damper | Room GF-04 | Proposed; OEM selection TBC
FSD-S04 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-04-01 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
SD-04-02 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
SD-04-03 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
RCD-R04 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R04 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-04-01 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
RG-04-02 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
RG-04-03 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
EH-04 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S08 | Supply branch balancing damper | Room GF-08 | Proposed; OEM selection TBC
FSD-S08 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-08-01 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-02 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-03 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-04 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-05 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-06 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
RCD-R08 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R08 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-08-01 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-02 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-03 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-04 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-05 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-06 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
VCD-S05 | Supply branch balancing damper | Room GF-05 | Proposed; OEM selection TBC
FSD-S05 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-05-01 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-02 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-03 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-04 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-05 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
RCD-R05 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R05 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-05-01 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-02 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-03 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-04 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-05 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
EH-05 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S06 | Supply branch balancing damper | Room GF-06 | Proposed; OEM selection TBC
FSD-S06 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-06-01 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
SD-06-02 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
SD-06-03 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
RCD-R06 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R06 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-06-01 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-02 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-03 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-04 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
EH-06 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S09 | Supply branch balancing damper | Room GF-09 | Proposed; OEM selection TBC
FSD-S09 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-09-01 | Supply diffuser with integral OBD | Room GF-09; 23.100 L/s | Proposed; OEM selection TBC
SD-09-02 | Supply diffuser with integral OBD | Room GF-09; 23.100 L/s | Proposed; OEM selection TBC
VCD-S07 | Supply branch balancing damper | Room GF-07 | Proposed; OEM selection TBC
FSD-S07 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-07-01 | Supply diffuser with integral OBD | Room GF-07; 168.200 L/s | Proposed; OEM selection TBC
RCD-R07 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R07 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-07-01 | Ducted return grille with OBD | Room GF-07; 108.863 L/s | Proposed; OEM selection TBC
EH-07 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S03 | Supply branch balancing damper | Room GF-03 | Proposed; OEM selection TBC
FSD-S03 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-03-01 | Supply diffuser with integral OBD | Room GF-03; 147.600 L/s | Proposed; OEM selection TBC
EH-03 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S01 | Supply branch balancing damper | Room GF-01 | Proposed; OEM selection TBC
FSD-S01 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-01-01 | Supply diffuser with integral OBD | Room GF-01; 141.300 L/s | Proposed; OEM selection TBC
EG-09-01 | Dedicated extract grille | GF-09; final pickup height / model TBC | Proposed; OEM selection TBC
EG-09-02 | Dedicated extract grille | GF-09; final pickup height / model TBC | Proposed; OEM selection TBC
MD-IE09-01 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-09-01 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E09-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
MD-IE09-02 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-09-02 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E09-02 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
EG-03-01 | Dedicated extract grille | GF-03; final pickup height / model TBC | Proposed; OEM selection TBC
MD-IE03-01 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-03-01 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E03-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
MD-IE03-02 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-03-02 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E03-02 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
EG-01-01 | Dedicated extract grille | GF-01; final pickup height / model TBC | Proposed; OEM selection TBC
EF-01-01 | Clean-agent extract fan | One fan shown; quantity / agent suitability TBC | Proposed; OEM selection TBC
MD-E01-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
HPCP-01 | Dedicated PLC HVAC power and control panel | 15.1 / 15.10 / 15.11; 20% spare I/O and CPU; separate duty / standby modules | Proposed; OEM selection TBC
HMI-01 | Local colour touchscreen HMI, >=10 inch | 15.12.1; alarms, trends, security, operating hours and energy | Proposed; OEM selection TBC
BMS-IF-01 | BMS / SCADA interface and operator workstation | 8.5.1 / 8.5.2; protocol and point mapping TBC | Proposed; OEM selection TBC
STL-01 | Outdoor sand trap louver / bird mesh | 7.12.1 / 7.7.1; mesh <=13 mm; SS316L when within 5 km of sea | Proposed; OEM selection TBC
F-OA-01 | Washable MERV 8 outdoor intake filter | 7.12.1; clean / dirty loss and face area TBC | Proposed; OEM selection TBC
OA-SIL-01 | Common outdoor intake sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
EA-SIL-03 | Dedicated extract sound attenuator | GF-03; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
EA-SIL-09 | Dedicated extract sound attenuator | GF-09; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
EA-SIL-01 | Dedicated extract sound attenuator | GF-01; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
STL-B1 | Cable basement sand trap louver / bird mesh | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
F-OA-B1 | Basement intake MERV 8 filter | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
OA-SIL-B1 | Basement intake sound attenuator | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
EA-SIL-B1-01 | Basement extract sound attenuator 1 | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
EA-SIL-B1-02 | Basement extract sound attenuator 2 | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
MD-OA-01 | Common outdoor-air modulating damper | Proposed minimum OA / building pressure control; final OA TBC | Proposed; OEM selection TBC
PRD-01 | Common outdoor relief path and relief control | 7.13 / user relief basis; Qrelief = QOA - 691.12 only under current assumed RA | Proposed; OEM selection TBC
SA-SIL-01 | Common supply sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
RA-SIL-01 | Common return sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
EH-COM-01 | Common electric duct heater in proposed weather-protected roof enclosure | 7.8.2; heating load / high-limit / airflow proof TBC | Rev11 roof option; OEM weather suitability / enclosure / safety / duty TBC
HUM-01 | Steam humidifier in main supply, if required | 7.10.1; conditional requirement / duty TBC | Rev11 proposed weather-protected roof plant; conditional duty / mounting / maintenance access TBC
PAU-A | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-A | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-A | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-A | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-A | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-A | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-A | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
PAU-B | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-B | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-B | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-B | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-B | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-B | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-B | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
PAU-C | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-C | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-C | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-C | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-C | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-C | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-C | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
SF-B1-01 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-SF-B1-01 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-ISF-B1-01 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
SF-B1-02 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-SF-B1-02 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-ISF-B1-02 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
EF-B1-01 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-EF-B1-01 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-IEF-B1-01 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
EF-B1-02 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-EF-B1-02 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-IEF-B1-02 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
AD-S02 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 02 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S08 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 08 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S09 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 09 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S03 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 03 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S01 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 01 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R02 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 02 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R08 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 08 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H03 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 03 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-HCOM-01 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater COM-01 | Rev11 proposed weather-protected roof plant; conditional duty / mounting / maintenance access TBC

## Mounting_baseline
tag | location | IO | proposed_range | mounting_detail | pressure_taps_or_straight_length | wiring_proposal | access | safety_or_commissioning | detail | status
TT-GF-02 | GF-02 Electrical panel | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-02 | GF-02 Electrical panel | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-02 | GF-02 Electrical panel | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-04 | GF-04 Meeting | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-04 | GF-04 Meeting | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-04 | GF-04 Meeting | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TSHH-EH-04 | EH-04 | DI | OEM heater manual-reset trip | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-08 | GF-08 Telecom panel | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-08 | GF-08 Telecom panel | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-08 | GF-08 Telecom panel | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-05 | GF-05 Operator console | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-05 | GF-05 Operator console | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-05 | GF-05 Operator console | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TSHH-EH-05 | EH-05 | DI | OEM heater manual-reset trip | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-06 | GF-06 Reception / corridor | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-06 | GF-06 Reception / corridor | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-06 | GF-06 Reception / corridor | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TSHH-EH-06 | EH-06 | DI | OEM heater manual-reset trip | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-09 | GF-09 Toilet group: two cubicles | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-09 | GF-09 Toilet group: two cubicles | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-09 | GF-09 Toilet group: two cubicles | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-07 | GF-07 Bedroom / Resting Room | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-07 | GF-07 Bedroom / Resting Room | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-07 | GF-07 Bedroom / Resting Room | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TSHH-EH-07 | EH-07 | DI | OEM heater manual-reset trip | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-03 | GF-03 Kitchen / kitchenette | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-03 | GF-03 Kitchen / kitchenette | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-03 | GF-03 Kitchen / kitchenette | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TSHH-EH-03 | EH-03 | DI | OEM heater manual-reset trip | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-GF-01 | GF-01 Clean-agent cylinder room | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-GF-01 | GF-01 Clean-agent cylinder room | AI | 0..100 %RH | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-GF-01 | GF-01 Clean-agent cylinder room | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-SA-01 | Common supply | AI | 0..50 degC | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-RA-01 | Common return | AI | 0..50 degC | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
RHT-RA-01 | Common return | AI | 0..100 %RH | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
FIT-SA-01 | Common supply straight length per manufacturer | AI | 0..5000 L/s | At selected equipment / duct; tag references D-012 to D-016 | OEM measurement array / station; reserve 5Dh upstream and 3Dh downstream as screening allowance, not approved OEM minimum | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
FIT-RA-01 | Common return straight length per manufacturer | AI | 0..5000 L/s | At selected equipment / duct; tag references D-012 to D-016 | OEM measurement array / station; reserve 5Dh upstream and 3Dh downstream as screening allowance, not approved OEM minimum | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDT-OA-01 | F-OA-01 | AI | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDI-OA-01 | F-OA-01 | LOCAL | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Local indication; no PLC channel | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TSHH-EH-COM-01 | EH-COM-01 | DI | OEM heater manual-reset trip | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDT-F1-A | PAU-A filter 1 | AI | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDI-F1-A | PAU-A filter 1 | LOCAL | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Local indication; no PLC channel | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDT-F2-A | PAU-A filter 2 | AI | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDI-F2-A | PAU-A filter 2 | LOCAL | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Local indication; no PLC channel | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-SF-A | PAU-A fan | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-PAU-A | PAU-A frame / fan bearing | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDT-F1-B | PAU-B filter 1 | AI | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDI-F1-B | PAU-B filter 1 | LOCAL | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Local indication; no PLC channel | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDT-F2-B | PAU-B filter 2 | AI | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDI-F2-B | PAU-B filter 2 | LOCAL | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Local indication; no PLC channel | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-SF-B | PAU-B fan | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-PAU-B | PAU-B frame / fan bearing | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDT-F1-C | PAU-C filter 1 | AI | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDI-F1-C | PAU-C filter 1 | LOCAL | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Local indication; no PLC channel | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDT-F2-C | PAU-C filter 2 | AI | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
PDI-F2-C | PAU-C filter 2 | LOCAL | 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Local indication; no PLC channel | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-SF-C | PAU-C fan | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-PAU-C | PAU-C frame / fan bearing | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-EF-03-01 | EF-03-01 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-EF-03-01 | EF-03-01 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-EF-03-02 | EF-03-02 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-EF-03-02 | EF-03-02 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-EF-09-01 | EF-09-01 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-EF-09-01 | EF-09-01 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-EF-09-02 | EF-09-02 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-EF-09-02 | EF-09-02 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-EF-01-01 | EF-01-01 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-EF-01-01 | EF-01-01 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-SF-B1-01 | SF-B1-01 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-SF-B1-01 | SF-B1-01 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-SF-B1-02 | SF-B1-02 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-SF-B1-02 | SF-B1-02 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-EF-B1-01 | EF-B1-01 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-EF-B1-01 | EF-B1-01 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-EF-B1-02 | EF-B1-02 | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) upstream; (-) downstream; separate labelled static taps and isolation / test ports; no facing-flow pickup | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
VS-EF-B1-02 | EF-B1-02 | AI | 0..25 mm/s RMS | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
TT-B1-01 | Cable basement | AI | 0..50 degC | Room sensor at +1.5 m AFFL away from supply jet / sunlight / heat source | Not applicable | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
DPT-B1-01 | Cable basement | AI | Room: -100..+100 Pa; fan: 0..1000 Pa | At selected equipment / duct; tag references D-012 to D-016 | (+) room static; (-) sheltered outdoor reference, common datum; prevent wind bias | Shielded twisted pair, 4-20 mA proposed; separate from power, shield earth at panel end; supply / isolator per OEM | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
EM-HPCP-01 | HPCP feeders >7.5 kW | COMM | Feeder voltage / CT ratio / protocol per approved electrical design | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Meter communication: protocol / address / isolation / termination TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Alarm settings, scaling and response approved during commissioning | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
AFS-EH-04 | Electric heater EH-04 | DI | OEM flow-proof setpoint | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
AFS-EH-05 | Electric heater EH-05 | DI | OEM flow-proof setpoint | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
AFS-EH-06 | Electric heater EH-06 | DI | OEM flow-proof setpoint | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
AFS-EH-07 | Electric heater EH-07 | DI | OEM flow-proof setpoint | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
AFS-EH-03 | Electric heater EH-03 | DI | OEM flow-proof setpoint | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending
AFS-EH-COM-01 | Electric heater EH-COM-01 | DI | OEM flow-proof setpoint | At selected equipment / duct; tag references D-012 to D-016 | Not applicable | Dry contact to DI proposed; OEM voltage / contact logic and final terminal IDs TBC | Maintain visible tag, reachable isolation / test / reset and equipment removal path; mounting-specific clearance per OEM | Hardwired heater safety chain; PLC demand cannot override AFS or independent high-limit; confirmed fire stops fans / heaters, manual reset | D-028 / D-029 | Proposed installation specification; OEM wiring and panel terminal numbers pending

## Roof_routes_Rev12
tag | air_type | role | room | points_mm | flow_l_s | width_mm | height_mm | length_m | velocity_m_s | friction_pa_m | proposed_bod_mm_affl | status | inlet_width_mm | inlet_height_mm | taper_length_mm
R-SA-M01 | SA | Roof main | COM | [[2300, 19000], [3600, 19000]] | 3697.8 | 600 | 1300 | 1.3 | 4.740769 | 0.26037 | 4800 | Proposed route / level; roof survey and structural approval pending | 600 | 1300 | 0
R-SA-02-04 | SA | Roof branch | 02 / 04 | [[3600, 19000], [3600, 16600.0]] | 1114.0 | 700 | 450 | 2.4 | 3.536508 | 0.247253 | 4800 | Proposed route / level; roof survey and structural approval pending | 700 | 450 | 0
R-SA-04A | SA | Roof branch | 04 | [[3600, 16600.0], [3600, 6500.0]] | 449.2 | 350.0 | 400.0 | 10.1 | 3.208571 | 0.330207 | 4800 | Proposed route / level; roof survey and structural approval pending | 700 | 450 | 675
R-SA-04B | SA | Roof branch | 04 | [[3600, 6500.0], [4200.0, 6500.0]] | 449.2 | 350.0 | 400.0 | 0.6 | 3.208571 | 0.330207 | 4800 | Proposed route / level; roof survey and structural approval pending | 350.0 | 400.0 | 0
R-SA-M02 | SA | Roof main | COM | [[3600, 19000], [8200, 19000]] | 2583.8 | 600 | 1300 | 4.6 | 3.312564 | 0.134355 | 4800 | Proposed route / level; roof survey and structural approval pending | 600 | 1300 | 0
R-SA-08A | SA | Roof branch | 08 | [[8200, 19000], [8200, 5600.0]] | 884.6 | 600.0 | 400.0 | 13.4 | 3.685833 | 0.313245 | 4800 | Proposed route / level; roof survey and structural approval pending | 600.0 | 400.0 | 0
R-SA-08B | SA | Roof branch | 08 | [[8200, 5600.0], [9800.0, 5600.0]] | 884.6 | 600.0 | 400.0 | 1.6 | 3.685833 | 0.313245 | 4800 | Proposed route / level; roof survey and structural approval pending | 600.0 | 400.0 | 0
R-SA-M03 | SA | Roof main | COM | [[8200, 19000], [12500, 19000]] | 1699.2 | 600 | 1300 | 4.3 | 2.178462 | 0.06241 | 4800 | Proposed route / level; roof survey and structural approval pending | 600 | 1300 | 0
R-SA-05-06 | SA | Roof branch | 05 / 06 | [[12500, 19000], [12500, 12800.0]] | 1195.9 | 700 | 400 | 6.2 | 4.271071 | 0.382462 | 4800 | Proposed route / level; roof survey and structural approval pending | 700 | 400 | 0
R-SA-06A | SA | Roof branch | 06 | [[12500, 12800.0], [12500, 9475.0]] | 418.2 | 450.0 | 300.0 | 3.325 | 3.097778 | 0.323797 | 4800 | Proposed route / level; roof survey and structural approval pending | 700 | 400 | 475
R-SA-M04 | SA | Roof main | COM | [[12500, 19000], [13400, 19000]] | 503.3 | 600 | 1300 | 0.9 | 0.645256 | 0.006985 | 4800 | Proposed route / level; roof survey and structural approval pending | 600 | 1300 | 0
R-SA-09A | SA | Roof branch | 09 | [[13400, 19000], [13400, 8200.0]] | 46.2 | 200.0 | 150.0 | 10.8 | 1.54 | 0.23071 | 4800 | Proposed route / level; roof survey and structural approval pending | 200.0 | 150.0 | 0
R-SA-M05 | SA | Roof main | COM | [[13400, 19000], [15500, 19000]] | 457.1 | 600 | 1300 | 2.1 | 0.586026 | 0.005886 | 4800 | Proposed route / level; roof survey and structural approval pending | 600 | 1300 | 0
R-SA-07A | SA | Roof branch | 07 | [[15500, 19000], [15500, 5000.0]] | 168.2 | 300.0 | 250.0 | 14.0 | 2.242667 | 0.253599 | 4800 | Proposed route / level; roof survey and structural approval pending | 300.0 | 250.0 | 0
R-SA-M06 | SA | Roof main | COM | [[15500, 19000], [17000, 19000]] | 288.9 | 600 | 1300 | 1.5 | 0.370385 | 0.002614 | 4800 | Proposed route / level; roof survey and structural approval pending | 600 | 1300 | 0
R-SA-03A | SA | Roof branch | 03 | [[17000, 19000], [17000, 7000.0]] | 147.6 | 300.0 | 200.0 | 12.0 | 2.46 | 0.351113 | 4800 | Proposed route / level; roof survey and structural approval pending | 300.0 | 200.0 | 0
R-SA-M07 | SA | Roof main | COM | [[17000, 19000], [18100, 19000]] | 141.3 | 600 | 1300 | 1.1 | 0.181154 | 0.000747 | 4800 | Proposed route / level; roof survey and structural approval pending | 600 | 1300 | 0
R-SA-01A | SA | Roof branch | 01 | [[18100, 19000], [18100, 3500.0]] | 141.3 | 300.0 | 200.0 | 15.5 | 2.355 | 0.324511 | 4800 | Proposed route / level; roof survey and structural approval pending | 300.0 | 200.0 | 0
R-SA-01B | SA | Roof branch | 01 | [[18100, 3500.0], [19400.0, 3500.0]] | 141.3 | 300.0 | 200.0 | 1.3 | 2.355 | 0.324511 | 4800 | Proposed route / level; roof survey and structural approval pending | 300.0 | 200.0 | 0
R-RA-M01 | RA | Roof main | COM | [[2700, 17000], [4800, 17000]] | 3006.68034 | 700 | 900 | 2.1 | 4.772508 | 0.27718 | 5550 | Proposed route / level; roof survey and structural approval pending | 700 | 900 | 0
R-RA-04A | RA | Roof branch | 04 | [[4800, 17000], [4800, 8250.0]] | 389.86339 | 500.0 | 350.0 | 8.75 | 2.227791 | 0.150816 | 5550 | Proposed route / level; roof survey and structural approval pending | 500.0 | 350.0 | 0
R-RA-M02 | RA | Roof main | COM | [[4800, 17000], [6000, 17000]] | 2616.81695 | 700 | 900 | 1.2 | 4.153678 | 0.214371 | 5550 | Proposed route / level; roof survey and structural approval pending | 700 | 900 | 0
R-RA-02A | RA | Roof branch | 02 | [[6000, 17000], [6000, 18150.0]] | 605.46339 | 650.0 | 400.0 | 1.15 | 2.328705 | 0.130368 | 5550 | Proposed route / level; roof survey and structural approval pending | 650.0 | 400.0 | 0
R-RA-M03 | RA | Roof main | COM | [[6000, 17000], [9400, 17000]] | 2011.35356 | 700 | 900 | 3.4 | 3.192625 | 0.132041 | 5550 | Proposed route / level; roof survey and structural approval pending | 700 | 900 | 0
R-RA-08A | RA | Roof branch | 08 | [[9400, 17000], [9400, 8450.0]] | 825.26339 | 850.0 | 400.0 | 8.55 | 2.427245 | 0.125343 | 5550 | Proposed route / level; roof survey and structural approval pending | 850.0 | 400.0 | 0
R-RA-M04 | RA | Roof main | COM | [[9400, 17000], [11300, 17000]] | 1186.09017 | 700 | 900 | 1.9 | 1.882683 | 0.050352 | 5550 | Proposed route / level; roof survey and structural approval pending | 700 | 900 | 0
R-RA-06A | RA | Roof branch | 06 | [[11300, 17000], [11300, 9800.0]] | 358.86339 | 500.0 | 400.0 | 7.2 | 1.794317 | 0.09286 | 5550 | Proposed route / level; roof survey and structural approval pending | 500.0 | 400.0 | 0
R-RA-M05 | RA | Roof main | COM | [[11300, 17000], [13000, 17000]] | 827.22678 | 700 | 900 | 1.7 | 1.313058 | 0.02624 | 5550 | Proposed route / level; roof survey and structural approval pending | 700 | 900 | 0
R-RA-07A | RA | Roof branch | 07 | [[13000, 17000], [13000, 5000.0]] | 108.86339 | 350.0 | 250.0 | 12.0 | 1.244153 | 0.081127 | 5550 | Proposed route / level; roof survey and structural approval pending | 350.0 | 250.0 | 0
R-RA-M06 | RA | Roof main | COM | [[13000, 17000], [19500, 17000]] | 718.36339 | 700 | 900 | 6.5 | 1.140259 | 0.020355 | 5550 | Proposed route / level; roof survey and structural approval pending | 700 | 900 | 0
R-RA-05A | RA | Roof branch | 05 | [[19500, 17000], [19500, 10400.0]] | 718.36339 | 700.0 | 400.0 | 6.6 | 2.565584 | 0.150333 | 5550 | Proposed route / level; roof survey and structural approval pending | 700.0 | 400.0 | 0

## Roof_risers
tag | branch | air_type | room | x_mm | y_mm | width_mm | height_mm | flow_l_s | indoor_bod_mm_affl | roof_bod_mm_affl | vertical_length_m | status | level_status
RS-SA02 | SA-B02 | SA | 02 | 3600 | 16600 | 500 | 350 | 664.8 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-RA02 | RA-B02 | RA | 02 | 6000 | 18150 | 650 | 400 | 605.46339 | 3400 | 5550 | 2.15 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA04 | SA-B04 | SA | 04 | 4200 | 6500 | 350 | 400 | 449.2 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-RA04 | RA-B04 | RA | 04 | 4800 | 8250 | 500 | 350 | 389.86339 | 3400 | 5550 | 2.15 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA08 | SA-B08 | SA | 08 | 9800 | 5600 | 600 | 400 | 884.6 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-RA08 | RA-B08 | RA | 08 | 9400 | 8450 | 850 | 400 | 825.26339 | 3400 | 5550 | 2.15 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA05 | SA-B05 | SA | 05 | 12500 | 12800 | 600 | 350 | 777.7 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-RA05 | RA-B05 | RA | 05 | 19500 | 10400 | 700 | 400 | 718.36339 | 3400 | 5550 | 2.15 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA06 | SA-B06 | SA | 06 | 12500 | 9475 | 450 | 300 | 418.2 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-RA06 | RA-B06 | RA | 06 | 11300 | 9800 | 500 | 400 | 358.86339 | 3400 | 5550 | 2.15 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA09 | SA-B09 | SA | 09 | 13400 | 8200 | 200 | 150 | 46.2 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA07 | SA-B07 | SA | 07 | 15500 | 5000 | 300 | 250 | 168.2 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-RA07 | RA-B07 | RA | 07 | 13000 | 5000 | 350 | 250 | 108.86339 | 3400 | 5550 | 2.15 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA03 | SA-B03 | SA | 03 | 17000 | 7000 | 300 | 200 | 147.6 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified
RS-SA01 | SA-B01 | SA | 01 | 19400 | 3500 | 300 | 200 | 141.3 | 3400 | 4800 | 1.4 | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending | PROPOSED: centerline rise with equal duct depth at both ends; roof thickness / beams / penetration and bend development unverified

## Common_main_sizing
tag | air_type | room_takeoff | flow_before_takeoff_l_s | takeoff_l_s | flow_after_takeoff_l_s | clear_width_mm | clear_depth_mm | velocity_m_s | straight_friction_pa_m | installed_length_m | status
SA-M01 | SA | 02 | 3697.8 | 664.8 | 3033.0 | 600 | 1300 | 4.740769 | 0.26037 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M02 | SA | 04 | 3033.0 | 449.2 | 2583.8 | 600 | 1300 | 3.888462 | 0.180483 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M03 | SA | 08 | 2583.8 | 884.6 | 1699.2000000000003 | 600 | 1300 | 3.312564 | 0.134355 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M04 | SA | 05 | 1699.2 | 777.7 | 921.5 | 600 | 1300 | 2.178462 | 0.06241 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M05 | SA | 06 | 921.5 | 418.2 | 503.3 | 600 | 1300 | 1.18141 | 0.020616 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M06 | SA | 09 | 503.3 | 46.2 | 457.1 | 600 | 1300 | 0.645256 | 0.006985 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M07 | SA | 07 | 457.1 | 168.2 | 288.90000000000003 | 600 | 1300 | 0.586026 | 0.005886 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M08 | SA | 03 | 288.9 | 147.6 | 141.29999999999998 | 600 | 1300 | 0.370385 | 0.002614 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
SA-M09 | SA | 01 | 141.3 | 141.3 | 0.0 | 600 | 1300 | 0.181154 | 0.000747 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
RA-M01 | RA | 02 | 3006.680337621642 | 605.463389603607 | 2401.216948018035 | 700 | 900 | 4.772508 | 0.27718 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
RA-M02 | RA | 04 | 2401.216948018035 | 389.863389603607 | 2011.353558414428 | 700 | 900 | 3.811455 | 0.182919 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
RA-M03 | RA | 08 | 2011.353558414428 | 825.263389603607 | 1186.090168810821 | 700 | 900 | 3.192625 | 0.132041 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
RA-M04 | RA | 05 | 1186.090168810821 | 718.3633896036071 | 467.726779207214 | 700 | 900 | 1.882683 | 0.050352 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
RA-M05 | RA | 06 | 467.726779207214 | 358.863389603607 | 108.863389603607 | 700 | 900 | 0.742423 | 0.009442 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012
RA-M06 | RA | 07 | 108.863389603607 | 108.863389603607 | 0.0 | 700 | 900 | 0.172799 | 0.000726 | TBC - surveyed route required | Functional sequential room-flow accounting only; actual grouped roof routes and 31 segment duties are in Roof_routes_Rev12 / MDR-012

## Additional_DX
tag | parameter | location | signal | action | range_or_setpoint | status
PSH-DX-A | DX discharge high pressure | PAU-A | OEM LOCAL | Hardwired compressor cutout; OEM reset / threshold | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PSL-DX-A | DX suction low pressure | PAU-A | OEM LOCAL | OEM low-pressure protection; refrigerant / operating envelope settings | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
TSLL-DX-A | Evaporator low temperature / frost protection | PAU-A | OEM LOCAL | OEM anti-freeze protection; fan / compressor response | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
LSH-DX-A | Condensate drain-pan overflow | PAU-A | DI proposal | OEM compressor inhibit / alarm; maintain drain access | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PT-SUC-DX-A | Suction refrigerant pressure | PAU-A | AI proposal | Monitor only if selected OEM permits pressure transmitter / factory data | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PT-LIQ-DX-A | Liquid refrigerant pressure | PAU-A | AI proposal | Monitor only if selected OEM permits pressure transmitter / factory data | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
OL-CMP-DX-A | Compressor overload protection | PAU-A | OEM LOCAL | Local motor protection; expose approved fault status | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PSH-DX-B | DX discharge high pressure | PAU-B | OEM LOCAL | Hardwired compressor cutout; OEM reset / threshold | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PSL-DX-B | DX suction low pressure | PAU-B | OEM LOCAL | OEM low-pressure protection; refrigerant / operating envelope settings | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
TSLL-DX-B | Evaporator low temperature / frost protection | PAU-B | OEM LOCAL | OEM anti-freeze protection; fan / compressor response | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
LSH-DX-B | Condensate drain-pan overflow | PAU-B | DI proposal | OEM compressor inhibit / alarm; maintain drain access | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PT-SUC-DX-B | Suction refrigerant pressure | PAU-B | AI proposal | Monitor only if selected OEM permits pressure transmitter / factory data | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PT-LIQ-DX-B | Liquid refrigerant pressure | PAU-B | AI proposal | Monitor only if selected OEM permits pressure transmitter / factory data | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
OL-CMP-DX-B | Compressor overload protection | PAU-B | OEM LOCAL | Local motor protection; expose approved fault status | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PSH-DX-C | DX discharge high pressure | PAU-C | OEM LOCAL | Hardwired compressor cutout; OEM reset / threshold | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PSL-DX-C | DX suction low pressure | PAU-C | OEM LOCAL | OEM low-pressure protection; refrigerant / operating envelope settings | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
TSLL-DX-C | Evaporator low temperature / frost protection | PAU-C | OEM LOCAL | OEM anti-freeze protection; fan / compressor response | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
LSH-DX-C | Condensate drain-pan overflow | PAU-C | DI proposal | OEM compressor inhibit / alarm; maintain drain access | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PT-SUC-DX-C | Suction refrigerant pressure | PAU-C | AI proposal | Monitor only if selected OEM permits pressure transmitter / factory data | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
PT-LIQ-DX-C | Liquid refrigerant pressure | PAU-C | AI proposal | Monitor only if selected OEM permits pressure transmitter / factory data | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
OL-CMP-DX-C | Compressor overload protection | PAU-C | OEM LOCAL | Local motor protection; expose approved fault status | OEM refrigerant / pressure-temperature envelope / electrical ratings TBC | NEW DX proposal, separate from 85 retained instruments; factory controller may expose approved contacts or communications
DPT-SA-M01 | Common supply duct static pressure | Common SA main; selected representative station | AI proposal | Optional static control only if OEM fan/VFD is suitable; maintain room scheduled minimum flow | 0..1000 Pa screening range; operating setpoint / station TBC | NEW DX option; does not override fire or OEM safeties

## Instrument_index
tag | parameter | location | io | graphical_sheet | status
TT-GF-02 | Dry bulb temperature | GF-02 Electrical panel | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-02 | Relative humidity | GF-02 Electrical panel | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-02 | Room pressure vs outdoor | GF-02 Electrical panel | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TT-GF-04 | Dry bulb temperature | GF-04 Meeting | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-04 | Relative humidity | GF-04 Meeting | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-04 | Room pressure vs outdoor | GF-04 Meeting | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TSHH-EH-04 | Heater high temperature limit | EH-04 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
TT-GF-08 | Dry bulb temperature | GF-08 Telecom panel | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-08 | Relative humidity | GF-08 Telecom panel | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-08 | Room pressure vs outdoor | GF-08 Telecom panel | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TT-GF-05 | Dry bulb temperature | GF-05 Operator console | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-05 | Relative humidity | GF-05 Operator console | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-05 | Room pressure vs outdoor | GF-05 Operator console | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TSHH-EH-05 | Heater high temperature limit | EH-05 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
TT-GF-06 | Dry bulb temperature | GF-06 Reception / corridor | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-06 | Relative humidity | GF-06 Reception / corridor | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-06 | Room pressure vs outdoor | GF-06 Reception / corridor | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TSHH-EH-06 | Heater high temperature limit | EH-06 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
TT-GF-09 | Dry bulb temperature | GF-09 Toilet group: two cubicles | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-09 | Relative humidity | GF-09 Toilet group: two cubicles | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-09 | Room pressure vs outdoor | GF-09 Toilet group: two cubicles | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TT-GF-07 | Dry bulb temperature | GF-07 Bedroom / Resting Room | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-07 | Relative humidity | GF-07 Bedroom / Resting Room | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-07 | Room pressure vs outdoor | GF-07 Bedroom / Resting Room | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TSHH-EH-07 | Heater high temperature limit | EH-07 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
TT-GF-03 | Dry bulb temperature | GF-03 Kitchen / kitchenette | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-03 | Relative humidity | GF-03 Kitchen / kitchenette | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-03 | Room pressure vs outdoor | GF-03 Kitchen / kitchenette | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TSHH-EH-03 | Heater high temperature limit | EH-03 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
TT-GF-01 | Dry bulb temperature | GF-01 Clean-agent cylinder room | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
RHT-GF-01 | Relative humidity | GF-01 Clean-agent cylinder room | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
DPT-GF-01 | Room pressure vs outdoor | GF-01 Clean-agent cylinder room | AI | MDR-006 | Retained requirement / settings and OEM wiring pending
TT-SA-01 | Supply air temperature | Common supply | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
TT-RA-01 | Return air temperature | Common return | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
RHT-RA-01 | Return relative humidity | Common return | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
FIT-SA-01 | Common supply airflow | Common supply straight length per manufacturer | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
FIT-RA-01 | Common return airflow | Common return straight length per manufacturer | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDT-OA-01 | Outdoor intake filter differential pressure | F-OA-01 | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDI-OA-01 | Local intake filter differential pressure gauge | F-OA-01 | LOCAL | MDR-004 | Retained requirement / settings and OEM wiring pending
TSHH-EH-COM-01 | Common heater high-limit | EH-COM-01 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
PDT-F1-A | Filter differential pressure | PAU-A filter 1 | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDI-F1-A | Local filter differential pressure gauge | PAU-A filter 1 | LOCAL | MDR-004 | Retained requirement / settings and OEM wiring pending
PDT-F2-A | Filter differential pressure | PAU-A filter 2 | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDI-F2-A | Local filter differential pressure gauge | PAU-A filter 2 | LOCAL | MDR-004 | Retained requirement / settings and OEM wiring pending
DPT-SF-A | Evaporator fan differential pressure | PAU-A fan | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
VS-PAU-A | RMS vibration velocity | PAU-A frame / fan bearing | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDT-F1-B | Filter differential pressure | PAU-B filter 1 | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDI-F1-B | Local filter differential pressure gauge | PAU-B filter 1 | LOCAL | MDR-004 | Retained requirement / settings and OEM wiring pending
PDT-F2-B | Filter differential pressure | PAU-B filter 2 | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDI-F2-B | Local filter differential pressure gauge | PAU-B filter 2 | LOCAL | MDR-004 | Retained requirement / settings and OEM wiring pending
DPT-SF-B | Evaporator fan differential pressure | PAU-B fan | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
VS-PAU-B | RMS vibration velocity | PAU-B frame / fan bearing | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDT-F1-C | Filter differential pressure | PAU-C filter 1 | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDI-F1-C | Local filter differential pressure gauge | PAU-C filter 1 | LOCAL | MDR-004 | Retained requirement / settings and OEM wiring pending
PDT-F2-C | Filter differential pressure | PAU-C filter 2 | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
PDI-F2-C | Local filter differential pressure gauge | PAU-C filter 2 | LOCAL | MDR-004 | Retained requirement / settings and OEM wiring pending
DPT-SF-C | Evaporator fan differential pressure | PAU-C fan | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
VS-PAU-C | RMS vibration velocity | PAU-C frame / fan bearing | AI | MDR-004 | Retained requirement / settings and OEM wiring pending
DPT-EF-03-01 | Extract fan pressure proof | EF-03-01 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
VS-EF-03-01 | RMS vibration velocity | EF-03-01 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
DPT-EF-03-02 | Extract fan pressure proof | EF-03-02 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
VS-EF-03-02 | RMS vibration velocity | EF-03-02 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
DPT-EF-09-01 | Extract fan pressure proof | EF-09-01 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
VS-EF-09-01 | RMS vibration velocity | EF-09-01 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
DPT-EF-09-02 | Extract fan pressure proof | EF-09-02 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
VS-EF-09-02 | RMS vibration velocity | EF-09-02 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
DPT-EF-01-01 | Extract fan pressure proof | EF-01-01 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
VS-EF-01-01 | RMS vibration velocity | EF-01-01 | AI | MDR-003 | Retained requirement / settings and OEM wiring pending
DPT-SF-B1-01 | Fan pressure proof | SF-B1-01 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
VS-SF-B1-01 | RMS vibration velocity | SF-B1-01 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
DPT-SF-B1-02 | Fan pressure proof | SF-B1-02 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
VS-SF-B1-02 | RMS vibration velocity | SF-B1-02 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
DPT-EF-B1-01 | Fan pressure proof | EF-B1-01 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
VS-EF-B1-01 | RMS vibration velocity | EF-B1-01 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
DPT-EF-B1-02 | Fan pressure proof | EF-B1-02 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
VS-EF-B1-02 | RMS vibration velocity | EF-B1-02 | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
TT-B1-01 | Cable basement air temperature | Cable basement | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
DPT-B1-01 | Basement pressure vs outdoor | Cable basement | AI | MDR-009 | Retained requirement / settings and OEM wiring pending
EM-HPCP-01 | Energy metering: V, I, kW, kWh, PF, Hz; THD for VFD | HPCP feeders >7.5 kW | COMM | MDR-009 | Retained requirement / settings and OEM wiring pending
AFS-EH-04 | Airflow proving switch for heater safety permissive | Electric heater EH-04 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
AFS-EH-05 | Airflow proving switch for heater safety permissive | Electric heater EH-05 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
AFS-EH-06 | Airflow proving switch for heater safety permissive | Electric heater EH-06 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
AFS-EH-07 | Airflow proving switch for heater safety permissive | Electric heater EH-07 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
AFS-EH-03 | Airflow proving switch for heater safety permissive | Electric heater EH-03 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending
AFS-EH-COM-01 | Airflow proving switch for heater safety permissive | Electric heater EH-COM-01 | DI | MDR-007 | Retained requirement / settings and OEM wiring pending