## Read_me
ADMINISTRATION HVAC - REV11 ROOF OPTION | 07 October 2026 ¦ engineering coordination option, not for construction
Drawings | 22 detailed A1 sheets; four functional schematic sheets. D-019 actual junctions; D-020 height envelope; D-021 changes; D-022 proposed roof drops.
User datums | Structural slab/roof underside +4.000 m; minimum ceiling / clear height +3.300 m. Verify AFFL and beam downstands on site.
Strategy | Roof common mains with 15 independent room drops. USER SELECTED ROOF DISTRIBUTION / ROOM DROPS. Actual roof routes and penetrations require structural / architectural coordination.
Indoor geometry | 116 indoor paths; nine supply, six return and two extract connected room trees; no indoor service crossings. Proposed bare BOD +3.400 m, bare depth <=400 mm.
Insulation | 50 mm each face assumed indoors, not a verified UAE standard. Deepest envelope: insulated top +3.850 m, bottom +3.350 m, slab allowance 150 mm and ceiling gap 50 mm.
Envelope limits | Only ducts checked: selected flanges, actuators, heater casings, supports, access and terminal plenums may require local redesign. Ceiling gap is not a general access / plenum allowance.
Roof_main_basis | Retained common-main flow / clear-size basis, functional only. Actual roof plan / lengths / BOD / outdoor insulation / weatherproofing and losses TBC.
Roof_risers | 15 proposed source-plan drop centers. No structural penetration approval, selected sleeves / curbs / fire rating or actual roof vertical development.
Revisions | 13 additional terminal position proposals and 20 existing section size changes relative to Rev10. New perimeter headers are included in route changes.
Sizing_check | All indoor velocities / plan centerline lengths / Colebrook straight friction recomputed. Not a complete fan ESP calculation; selected fitting K and roof / vertical lengths pending.
Instrumentation | 85 requirements and I/O duties retained. Common probes / heater / conditional humidifier move to proposed weather-protected roof plant. Five common probes shown functionally on D-012, not physically located on an unsurveyed roof.
Pressure / OA | SA 3697.80 L/s; assumed RA 3006.68 L/s. OA reference 420.70 vs 691.12 implied makeup. Toilet net -18.69 L/s and kitchen zero do not prove +25 Pa.
Access / protection | 20 proposed indoor AD plan tags plus AD-HCOM-01 in roof plant schematic. OEM dimensions and working access, conditional fire boundaries and final wiring remain open.
History | Rev08 / Rev09 / Rev10 originals retained. Rev10 stacked crossing CX-08 bottom +2.050 m fails new +3.300 m requirement and is superseded for this option.
Editing | Edit source CSV/JSON together and regenerate. Excel-only edits are not imported. Do not rerun revision migrations after editing prepared inputs.

## Duct_sections
tag | air_type | role | room | flow_l_s | width_mm | height_mm | diameter_mm | velocity_m_s | friction_pa_m | horizontal_length_m | vertical_length_m | level | route_basis | points_mm | zone | proposed_bod_mm_affl | level_status
SA-B02 | SA | Branch | 02 | 664.8 | 500 | 350 |  | 3.79886 | 0.3991 | 1.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[3600, 16600], [4800, 16600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H02-U01 | SA | Room header | 02 | 332.4 | 500 | 350 |  | 1.89943 | 0.11304 | 1.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 16600], [4800, 17700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H02-D01 | SA | Room header | 02 | 332.4 | 500 | 350 |  | 1.89943 | 0.11304 | 3.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 16600], [4800, 13100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R02-01 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 17700], [2700, 17700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R02-02 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 17700], [7100, 17700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R02-03 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 13100], [2700, 13100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R02-04 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 13100], [7100, 13100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-B02 | RA | Branch | 02 | 605.46339 | 650 | 400 |  | 2.32871 | 0.13037 | 0.95 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[6000, 19100], [6000, 18150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H02-U01 | RA | Room header | 02 | 302.731695 | 450 | 350 |  | 1.92211 | 0.12202 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[1500, 17000], [1500, 19100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H02-D01 | RA | Room header | 02 | 151.365848 | 450 | 350 |  | 0.96105 | 0.03526 | 5.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[1500, 11900], [1500, 17000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R02-01 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 0.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2000, 17000], [1500, 17000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R02-02 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 0.35 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[7700, 17000], [8050, 17000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R02-03 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 0.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2000, 11900], [1500, 11900]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R02-04 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 0.35 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[7700, 11900], [8050, 11900]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B04 | SA | Branch | 04 | 449.2 | 350 | 400 |  | 3.20857 | 0.33021 | 1.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4200, 6500], [2900, 6500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H04-U01 | SA | Room header | 04 | 149.733333 | 450 | 300 |  | 1.10914 | 0.05087 | 0.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2900, 6500], [2900, 6600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H04-D01 | SA | Room header | 04 | 299.466667 | 450 | 300 |  | 2.21827 | 0.17652 | 2.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2900, 6500], [2900, 4300]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H04-D02 | SA | Room header | 04 | 149.733333 | 450 | 300 |  | 1.10914 | 0.05087 | 2.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2900, 4300], [2900, 1900]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R04-01 | SA | Runout | 04 | 149.733333 | 325 |  | 325 | 1.80494 | 0.13805 | 1.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2900, 6600], [1800, 6600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R04-02 | SA | Runout | 04 | 149.733333 | 325 |  | 325 | 1.80494 | 0.13805 | 1.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2900, 4300], [4100, 4300]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R04-03 | SA | Runout | 04 | 149.733333 | 325 |  | 325 | 1.80494 | 0.13805 | 1.0 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[2900, 1900], [1900, 1900]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-B04 | RA | Branch | 04 | 389.86339 | 500 | 350 |  | 2.22779 | 0.15082 | 0.95 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 7300], [4800, 8250]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H04-U01 | RA | Room header | 04 | 389.86339 | 500 | 350 |  | 2.22779 | 0.15082 | 0.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 7200], [4800, 7300]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H04-D01 | RA | Room header | 04 | 259.908926 | 500 | 350 |  | 1.48519 | 0.0726 | 2.9 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 4300], [4800, 7200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H04-D02 | RA | Room header | 04 | 129.954463 | 500 | 350 |  | 0.7426 | 0.02111 | 3.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4800, 1000], [4800, 4300]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R04-01 | RA | Runout | 04 | 129.954463 | 300 |  | 300 | 1.83848 | 0.15755 | 4.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[700, 7200], [4800, 7200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R04-02 | RA | Runout | 04 | 129.954463 | 300 |  | 300 | 1.83848 | 0.15755 | 0.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5000, 4300], [4800, 4300]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R04-03 | RA | Runout | 04 | 129.954463 | 300 |  | 300 | 1.83848 | 0.15755 | 4.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[700, 1000], [4800, 1000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B08 | SA | Branch | 08 | 884.6 | 600 | 400 |  | 3.68583 | 0.31325 | 1.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9800, 5600], [8500, 5600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H08-U01 | SA | Room header | 08 | 294.866667 | 600 | 400 |  | 1.22861 | 0.04276 | 0.9 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 5600], [8500, 6500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H08-D01 | SA | Room header | 08 | 589.733333 | 600 | 400 |  | 2.45722 | 0.14933 | 1.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 5600], [8500, 4200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H08-D02 | SA | Room header | 08 | 294.866667 | 600 | 400 |  | 1.22861 | 0.04276 | 2.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 4200], [8500, 1700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R08-01 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 1.7 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 6500], [6800, 6500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R08-02 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 6500], [10600, 6500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R08-03 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 1.7 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 4200], [6800, 4200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R08-04 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 4200], [10600, 4200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R08-05 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 1.7 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 1700], [6800, 1700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R08-06 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8500, 1700], [10600, 1700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-B08 | RA | Branch | 08 | 825.26339 | 850 | 400 |  | 2.42725 | 0.12534 | 0.95 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9400, 7500], [9400, 8450]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-U01 | RA | Room header | 08 | 412.631695 | 500 | 350 |  | 2.3579 | 0.16716 | 0.35 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5800, 7150], [5800, 7500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-D01 | RA | Room header | 08 | 275.087797 | 500 | 350 |  | 1.57193 | 0.08039 | 2.55 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5800, 4600], [5800, 7150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-D02 | RA | Room header | 08 | 137.543898 | 500 | 350 |  | 0.78597 | 0.02334 | 3.7 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5800, 900], [5800, 4600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R08-01 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 0.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5500, 7150], [5800, 7150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R08-02 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 0.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11400, 7150], [11500, 7150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R08-03 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 0.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5500, 4600], [5800, 4600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R08-04 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 0.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11400, 4600], [11500, 4600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R08-05 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 0.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5500, 900], [5800, 900]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R08-06 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 0.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11400, 900], [11500, 900]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B05 | SA | Branch | 05 | 777.7 | 600 | 350 |  | 3.70333 | 0.34926 | 1.9 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[12500, 12800], [14000, 12800], [14000, 13200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H05-U01 | SA | Room header | 05 | 777.7 | 600 | 350 |  | 3.70333 | 0.34926 | 0.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 13200], [14000, 13600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H05-U02 | SA | Room header | 05 | 466.62 | 600 | 350 |  | 2.222 | 0.13757 | 2.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 13600], [14000, 15800]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H05-U03 | SA | Room header | 05 | 311.08 | 600 | 350 |  | 1.48133 | 0.06619 | 2.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 15800], [14000, 18100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R05-01 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 3.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 18100], [10900, 18100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R05-02 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 2.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 18100], [16600, 18100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R05-03 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 4.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 15800], [18300, 15800]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R05-04 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 3.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 13600], [10900, 13600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R05-05 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 2.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14000, 13600], [16600, 13600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-B05 | RA | Branch | 05 | 718.36339 | 700 | 400 |  | 2.56558 | 0.15033 | 1.0 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19500, 11400], [19500, 10400]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H05-U01 | RA | Room header | 05 | 574.690712 | 700 | 400 |  | 2.05247 | 0.10024 | 0.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19500, 12500], [19500, 12000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H05-U02 | RA | Room header | 05 | 431.018034 | 700 | 400 |  | 1.53935 | 0.05962 | 6.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19500, 18800], [19500, 12500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H05-U03 | RA | Room header | 05 | 287.345356 | 700 | 400 |  | 1.02623 | 0.02882 | 0.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19500, 19000], [19500, 18800]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H05-D01 | RA | Room header | 05 | 143.672678 | 700 | 400 |  | 0.51312 | 0.00843 | 4.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9600, 14600], [9600, 18800]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R05-01 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 0.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9900, 18800], [9600, 18800]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R05-02 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 0.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19000, 18800], [19500, 18800]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R05-03 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 0.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9900, 14600], [9600, 14600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R05-04 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 0.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19000, 12500], [19500, 12500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R05-05 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 4.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[15100, 12000], [19500, 12000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B06 | SA | Branch | 06 | 418.2 | 450 | 300 |  | 3.09778 | 0.3238 | 1.225 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[12500, 9475], [12500, 10700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H06-D01 | SA | Room header | 06 | 139.4 | 450 | 300 |  | 1.03259 | 0.04479 | 7.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[12500, 10700], [5400, 10700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R06-01 | SA | Runout | 06 | 139.4 | 300 |  | 300 | 1.97211 | 0.17876 | 0.55 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5400, 10700], [5400, 10150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R06-02 | SA | Runout | 06 | 139.4 | 300 |  | 300 | 1.97211 | 0.17876 | 0.55 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14700, 10700], [14700, 10150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R06-03 | SA | Runout | 06 | 139.4 | 300 |  | 300 | 1.97211 | 0.17876 | 0.55 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[18300, 10700], [18300, 10150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-B06 | RA | Branch | 06 | 358.86339 | 500 | 400 |  | 1.79432 | 0.09286 | 0.95 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11300, 8850], [11300, 9800]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H06-D01 | RA | Room header | 06 | 179.431695 | 500 | 400 |  | 0.89716 | 0.02684 | 5.9 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[17200, 8850], [11300, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R06-01 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 0.025 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4500, 8875], [4500, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R06-02 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 0.025 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9700, 8875], [9700, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R06-03 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 0.025 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[17200, 8875], [17200, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R06-04 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 0.025 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[18300, 8875], [18300, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B09 | SA | Branch | 09 | 46.2 | 200 | 150 |  | 1.54 | 0.23071 | 0.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[13400, 8200], [13400, 7600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H09-D01 | SA | Room header | 09 | 46.2 | 200 | 150 |  | 1.54 | 0.23071 | 0.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[13400, 7600], [13400, 7000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H09-D02 | SA | Room header | 09 | 23.1 | 200 | 150 |  | 0.77 | 0.06797 | 1.8 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[13400, 7000], [13400, 5200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R09-01 | SA | Runout | 09 | 23.1 | 150 |  | 150 | 1.30719 | 0.20416 | 0.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[13400, 7000], [13600, 7000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R09-02 | SA | Runout | 09 | 23.1 | 150 |  | 150 | 1.30719 | 0.20416 | 0.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[13400, 5200], [13600, 5200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B07 | SA | Branch | 07 | 168.2 | 300 | 250 |  | 2.24267 | 0.2536 | 2.8 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[15500, 5000], [15500, 3600], [14100, 3600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H07-D01 | SA | Room header | 07 | 168.2 | 300 | 250 |  | 2.24267 | 0.2536 | 0.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14100, 3600], [14100, 3200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R07-01 | SA | Runout | 07 | 168.2 | 350 |  | 350 | 1.74824 | 0.11894 | 0.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14100, 3200], [13900, 3200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-B07 | RA | Branch | 07 | 108.86339 | 350 | 250 |  | 1.24415 | 0.08113 | 2.8 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[13000, 2200], [13000, 5000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H07-D01 | RA | Room header | 07 | 108.86339 | 350 | 250 |  | 1.24415 | 0.08113 | 0.8 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[13000, 1400], [13000, 2200]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-R07-01 | RA | Runout | 07 | 108.86339 | 300 |  | 300 | 1.5401 | 0.11467 | 1.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14400, 1400], [13000, 1400]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B03 | SA | Branch | 03 | 147.6 | 300 | 200 |  | 2.46 | 0.35111 | 1.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[17000, 7000], [18200, 7000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H03-D01 | SA | Room header | 03 | 147.6 | 300 | 200 |  | 2.46 | 0.35111 | 0.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[18200, 7000], [18200, 6600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R03-01 | SA | Runout | 03 | 147.6 | 325 |  | 325 | 1.77922 | 0.13453 | 0.4 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[18200, 6600], [18600, 6600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-B01 | SA | Branch | 01 | 141.3 | 300 | 200 |  | 2.355 | 0.32451 | 2.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19400, 3500], [16800, 3500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H01-D01 | SA | Room header | 01 | 141.3 | 300 | 200 |  | 2.355 | 0.32451 | 0.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[16800, 3500], [16800, 3000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-R01-01 | SA | Runout | 01 | 141.3 | 300 |  | 300 | 1.99899 | 0.18317 | 1.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[16800, 3000], [18100, 3000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
EA-B09 | EA | Extract branch | 09 | 64.888889 | 250 | 200 |  | 1.29778 | 0.12286 | 6.7 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14700, 7000], [14700, 7600], [20800, 7600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
EA-R09-01 | EA | Extract runout | 09 | 32.444444 | 150 |  | 150 | 1.83598 | 0.37327 | 0.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14200, 7000], [14700, 7000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
EA-R09-02 | EA | Extract runout | 09 | 32.444444 | 150 |  | 150 | 1.83598 | 0.37327 | 2.3 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14200, 5200], [14700, 5200], [14700, 7000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
EA-B03 | EA | Extract branch | 03 | 147.6 | 300 | 200 |  | 2.46 | 0.35111 | 1.9 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[18900, 5700], [20800, 5700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H05-L01 | RA | Room header | 05 | 287.345356 | 700 | 400 |  | 1.02623 | 0.02882 | 0.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9600, 18800], [9600, 19000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H05-N01 | RA | Room header | 05 | 287.345356 | 700 | 400 |  | 1.02623 | 0.02882 | 9.9 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9600, 19000], [19500, 19000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H05-E01 | RA | Room header | 05 | 718.36339 | 700 | 400 |  | 2.56558 | 0.15033 | 0.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[19500, 12000], [19500, 11400]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H06-E01 | SA | Room header | 06 | 278.8 | 450 | 300 |  | 2.06519 | 0.15511 | 2.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[12500, 10700], [14700, 10700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
SA-H06-E02 | SA | Room header | 06 | 139.4 | 450 | 300 |  | 1.03259 | 0.04479 | 3.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[14700, 10700], [18300, 10700]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H06-L01 | RA | Room header | 06 | 89.715847 | 500 | 400 |  | 0.44858 | 0.0079 | 5.2 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[4500, 8850], [9700, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H06-L02 | RA | Room header | 06 | 179.431695 | 500 | 400 |  | 0.89716 | 0.02684 | 1.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[9700, 8850], [11300, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H06-E01 | RA | Room header | 06 | 89.715847 | 500 | 400 |  | 0.44858 | 0.0079 | 1.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[18300, 8850], [17200, 8850]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H02-E01 | RA | Room header | 02 | 151.365848 | 450 | 350 |  | 0.96105 | 0.03526 | 5.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8050, 11900], [8050, 17000]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H02-E02 | RA | Room header | 02 | 302.731695 | 450 | 350 |  | 1.92211 | 0.12202 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8050, 17000], [8050, 19100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H02-N01 | RA | Room header | 02 | 302.731695 | 450 | 350 |  | 1.92211 | 0.12202 | 4.5 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[1500, 19100], [6000, 19100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H02-N02 | RA | Room header | 02 | 302.731695 | 450 | 350 |  | 1.92211 | 0.12202 | 2.05 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[8050, 19100], [6000, 19100]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-E01 | RA | Room header | 08 | 137.543898 | 500 | 350 |  | 0.78597 | 0.02334 | 3.7 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11500, 900], [11500, 4600]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-E02 | RA | Room header | 08 | 275.087797 | 500 | 350 |  | 1.57193 | 0.08039 | 2.55 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11500, 4600], [11500, 7150]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-E03 | RA | Room header | 08 | 412.631695 | 500 | 350 |  | 2.3579 | 0.16716 | 0.35 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11500, 7150], [11500, 7500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-N01 | RA | Room header | 08 | 412.631695 | 500 | 350 |  | 2.3579 | 0.16716 | 3.6 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[5800, 7500], [9400, 7500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending
RA-H08-N02 | RA | Room header | 08 | 412.631695 | 500 | 350 |  | 2.3579 | 0.16716 | 2.1 | TBC | Bare BOD +3.400 m proposed | Rev11 roof-main option, independent room riser; geometry and local envelope proposal, actual roof routing / structural penetrations / ESP / OEM selection pending | [[11500, 7500], [9400, 7500]] | INDOOR | 3400 | Proposed bare BOD; OEM flanges / terminal plenums / beams / access pending

## Transitions
tag | type | air | upstream | downstream | start_x_mm | start_y_mm | end_x_mm | end_y_mm | plan_mouth_mm | plan_neck_mm | proposed_length_mm | status
TR-SA-R02-01 | Rectangular-to-round terminal adaptor | SA | SA-H02-U01 | SA-R02-01 | 4550.0 | 17700.0 | 4250.0 | 17700.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R02-02 | Rectangular-to-round terminal adaptor | SA | SA-H02-U01 | SA-R02-02 | 5050.0 | 17700.0 | 5350.0 | 17700.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R02-03 | Rectangular-to-round terminal adaptor | SA | SA-H02-D01 | SA-R02-03 | 4550.0 | 13100.0 | 4250.0 | 13100.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R02-04 | Rectangular-to-round terminal adaptor | SA | SA-H02-D01 | SA-R02-04 | 5050.0 | 13100.0 | 5350.0 | 13100.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R02-01 | Rectangular-to-round terminal adaptor | RA | RA-R02-01 | RA-H02-U01 | 1725.0 | 17000.0 | 1835.0 | 17000.0 | 375 | 300 | 110 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R02-03 | Rectangular-to-round terminal adaptor | RA | RA-R02-03 | RA-H02-D01 | 1725.0 | 11900.0 | 1835.0 | 11900.0 | 375 | 300 | 110 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R04-01 | Rectangular-to-round terminal adaptor | SA | SA-H04-U01 | SA-R04-01 | 2675.0 | 6600.0 | 2375.0 | 6600.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R04-02 | Rectangular-to-round terminal adaptor | SA | SA-H04-D01 | SA-R04-02 | 3125.0 | 4300.0 | 3425.0 | 4300.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R04-03 | Rectangular-to-round terminal adaptor | SA | SA-H04-D02 | SA-R04-03 | 2675.0 | 1900.0 | 2375.0 | 1900.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R04-01 | Rectangular-to-round terminal adaptor | RA | RA-R04-01 | RA-H04-U01 | 4550.0 | 7200.0 | 4250.0 | 7200.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R04-03 | Rectangular-to-round terminal adaptor | RA | RA-R04-03 | RA-H04-D02 | 4550.0 | 1000.0 | 4250.0 | 1000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-01 | Rectangular-to-round terminal adaptor | SA | SA-H08-U01 | SA-R08-01 | 8200.0 | 6500.0 | 7900.0 | 6500.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-02 | Rectangular-to-round terminal adaptor | SA | SA-H08-U01 | SA-R08-02 | 8800.0 | 6500.0 | 9100.0 | 6500.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-03 | Rectangular-to-round terminal adaptor | SA | SA-H08-D01 | SA-R08-03 | 8200.0 | 4200.0 | 7900.0 | 4200.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-04 | Rectangular-to-round terminal adaptor | SA | SA-H08-D01 | SA-R08-04 | 8800.0 | 4200.0 | 9100.0 | 4200.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-05 | Rectangular-to-round terminal adaptor | SA | SA-H08-D02 | SA-R08-05 | 8200.0 | 1700.0 | 7900.0 | 1700.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-06 | Rectangular-to-round terminal adaptor | SA | SA-H08-D02 | SA-R08-06 | 8800.0 | 1700.0 | 9100.0 | 1700.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-01 | Rectangular-to-round terminal adaptor | SA | SA-H05-U03 | SA-R05-01 | 13700.0 | 18100.0 | 13400.0 | 18100.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-02 | Rectangular-to-round terminal adaptor | SA | SA-H05-U03 | SA-R05-02 | 14300.0 | 18100.0 | 14600.0 | 18100.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-03 | Rectangular-to-round terminal adaptor | SA | SA-H05-U02 | SA-R05-03 | 14300.0 | 15800.0 | 14600.0 | 15800.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-04 | Rectangular-to-round terminal adaptor | SA | SA-H05-U01 | SA-R05-04 | 13700.0 | 13600.0 | 13400.0 | 13600.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-05 | Rectangular-to-round terminal adaptor | SA | SA-H05-U01 | SA-R05-05 | 14300.0 | 13600.0 | 14600.0 | 13600.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R05-05 | Rectangular-to-round terminal adaptor | RA | RA-R05-05 | RA-H05-U01 | 19150.0 | 12000.0 | 18850.0 | 12000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R06-01 | Rectangular-to-round terminal adaptor | SA | SA-H06-D01 | SA-R06-01 | 5400.0 | 10475.0 | 5400.0 | 10345.0 | 375 | 300 | 130 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R06-02 | Rectangular-to-round terminal adaptor | SA | SA-H06-E01 | SA-R06-02 | 14700.0 | 10475.0 | 14700.0 | 10345.0 | 375 | 300 | 130 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R06-03 | Rectangular-to-round terminal adaptor | SA | SA-H06-E02 | SA-R06-03 | 18300.0 | 10475.0 | 18300.0 | 10345.0 | 375 | 300 | 130 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R07-01 | Rectangular-to-round terminal adaptor | RA | RA-R07-01 | RA-H07-D01 | 13175.0 | 1400.0 | 13475.0 | 1400.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R03-01 | Rectangular-to-round terminal adaptor | SA | SA-H03-D01 | SA-R03-01 | 18350.0 | 6600.0 | 18450.0 | 6600.0 | 406 | 325 | 100 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R01-01 | Rectangular-to-round terminal adaptor | SA | SA-H01-D01 | SA-R01-01 | 16950.0 | 3000.0 | 17250.0 | 3000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-EA-R09-01 | Rectangular-to-round terminal adaptor | EA | EA-R09-01 | EA-B09 | 14575.0 | 7000.0 | 14425.0 | 7000.0 | 188 | 150 | 150 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-EA-R09-02 | Rectangular-to-round terminal adaptor | EA | EA-R09-02 | EA-B09 | 14700.0 | 7000.0 | 14700.0 | 6700.0 | 250 | 150 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC

## Fittings
tag | section | type | x_mm | y_mm | loss_K | basis
F-SA-B05-B01 | SA-B05 | Radius / vaned elbow - see actual plan envelope | 14000 | 12800 | TBC selected fitting | Rev11 route vertex; selected radius / turning vanes and vertical development require approval
F-SA-B07-B01 | SA-B07 | Radius / vaned elbow - see actual plan envelope | 15500 | 3600 | TBC selected fitting | Rev11 route vertex; selected radius / turning vanes and vertical development require approval
F-EA-B09-B01 | EA-B09 | Radius / vaned elbow - see actual plan envelope | 14700 | 7600 | TBC selected fitting | Rev11 route vertex; selected radius / turning vanes and vertical development require approval
F-EA-R09-02-B01 | EA-R09-02 | Radius / vaned elbow - see actual plan envelope | 14700 | 5200 | TBC selected fitting | Rev11 route vertex; selected radius / turning vanes and vertical development require approval
TR-SA-R02-01 | SA-R02-01 | Rectangular-to-round terminal adaptor | 4400.0 | 17700.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R02-02 | SA-R02-02 | Rectangular-to-round terminal adaptor | 5200.0 | 17700.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R02-03 | SA-R02-03 | Rectangular-to-round terminal adaptor | 4400.0 | 13100.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R02-04 | SA-R02-04 | Rectangular-to-round terminal adaptor | 5200.0 | 13100.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-RA-R02-01 | RA-R02-01 | Rectangular-to-round terminal adaptor | 1780.0 | 17000.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 110 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-RA-R02-03 | RA-R02-03 | Rectangular-to-round terminal adaptor | 1780.0 | 11900.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 110 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R04-01 | SA-R04-01 | Rectangular-to-round terminal adaptor | 2525.0 | 6600.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R04-02 | SA-R04-02 | Rectangular-to-round terminal adaptor | 3275.0 | 4300.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R04-03 | SA-R04-03 | Rectangular-to-round terminal adaptor | 2525.0 | 1900.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-RA-R04-01 | RA-R04-01 | Rectangular-to-round terminal adaptor | 4400.0 | 7200.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-RA-R04-03 | RA-R04-03 | Rectangular-to-round terminal adaptor | 4400.0 | 1000.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R08-01 | SA-R08-01 | Rectangular-to-round terminal adaptor | 8050.0 | 6500.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R08-02 | SA-R08-02 | Rectangular-to-round terminal adaptor | 8950.0 | 6500.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R08-03 | SA-R08-03 | Rectangular-to-round terminal adaptor | 8050.0 | 4200.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R08-04 | SA-R08-04 | Rectangular-to-round terminal adaptor | 8950.0 | 4200.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R08-05 | SA-R08-05 | Rectangular-to-round terminal adaptor | 8050.0 | 1700.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R08-06 | SA-R08-06 | Rectangular-to-round terminal adaptor | 8950.0 | 1700.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R05-01 | SA-R05-01 | Rectangular-to-round terminal adaptor | 13550.0 | 18100.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R05-02 | SA-R05-02 | Rectangular-to-round terminal adaptor | 14450.0 | 18100.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R05-03 | SA-R05-03 | Rectangular-to-round terminal adaptor | 14450.0 | 15800.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R05-04 | SA-R05-04 | Rectangular-to-round terminal adaptor | 13550.0 | 13600.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R05-05 | SA-R05-05 | Rectangular-to-round terminal adaptor | 14450.0 | 13600.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-RA-R05-05 | RA-R05-05 | Rectangular-to-round terminal adaptor | 19000.0 | 12000.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R06-01 | SA-R06-01 | Rectangular-to-round terminal adaptor | 5400.0 | 10410.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 130 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R06-02 | SA-R06-02 | Rectangular-to-round terminal adaptor | 14700.0 | 10410.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 130 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R06-03 | SA-R06-03 | Rectangular-to-round terminal adaptor | 18300.0 | 10410.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 130 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-RA-R07-01 | RA-R07-01 | Rectangular-to-round terminal adaptor | 13325.0 | 1400.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R03-01 | SA-R03-01 | Rectangular-to-round terminal adaptor | 18400.0 | 6600.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 100 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-R01-01 | SA-R01-01 | Rectangular-to-round terminal adaptor | 17100.0 | 3000.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-EA-R09-01 | EA-R09-01 | Rectangular-to-round terminal adaptor | 14500.0 | 7000.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 150 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-EA-R09-02 | EA-R09-02 | Rectangular-to-round terminal adaptor | 14700.0 | 6850.0 | TBC selected fitting | Rev11 replacement profile; proposed axial length 300 mm; clear W x H / D per sections; fitting K and fabrication development pending
TR-SA-B06 | SA-B06 | Formed straight branch take-off | 12500 | 9475 | TBC selected fitting | Straight common station for corridor devices; selected fitting / access and OEM face-to-face dimensions pending
TR-RA-B06 | RA-B06 | Formed straight branch take-off | 11300 | 9800 | TBC selected fitting | Straight common station for corridor devices; selected fitting / access and OEM face-to-face dimensions pending

## Terminals
tag | room | air_type | flow_l_s | neck_dia_mm | face_w_mm | face_h_mm | x_mm | y_mm | level | catalogue
SD-02-01 | 02 | SA | 166.2 | 350 | 600 | 600 | 2700 | 17700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-02 | 02 | SA | 166.2 | 350 | 600 | 600 | 7100 | 17700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-03 | 02 | SA | 166.2 | 350 | 600 | 600 | 2700 | 13100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-04 | 02 | SA | 166.2 | 350 | 600 | 600 | 7100 | 13100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-02-01 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 2000 | 17000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-02 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 7700 | 17000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-03 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 2000 | 11900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-04 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 7700 | 11900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-04-01 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 1800 | 6600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-04-02 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 4100 | 4300 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-04-03 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 1900 | 1900 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-04-01 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 700 | 7200 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-04-02 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 5000 | 4300 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-04-03 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 700 | 1000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-08-01 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6800 | 6500 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-02 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 6500 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-03 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6800 | 4200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-04 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 4200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-05 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6800 | 1700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-06 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 1700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-08-01 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5500 | 7150 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-02 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11400 | 7150 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-03 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5500 | 4600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-04 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11400 | 4600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-05 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5500 | 900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-06 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11400 | 900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-05-01 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 10900 | 18100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-02 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 16600 | 18100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-03 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 18300 | 15800 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-04 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 10900 | 13600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-05 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 16600 | 13600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-05-01 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 9900 | 18800 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-02 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 19000 | 18800 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-03 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 9900 | 14600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-04 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 19000 | 12500 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-05 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 15100 | 12000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-06-01 | 06 | SA | 139.4 | 300 | 600 | 600 | 5400 | 10150 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-06-02 | 06 | SA | 139.4 | 300 | 600 | 600 | 14700 | 10150 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-06-03 | 06 | SA | 139.4 | 300 | 600 | 600 | 18300 | 10150 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-06-01 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 4500 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-02 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 9700 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-03 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 17200 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-04 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 18300 | 8875 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-09-01 | 09 | SA | 23.1 | 150 | 300 | 300 | 13600 | 7000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-09-02 | 09 | SA | 23.1 | 150 | 300 | 300 | 13600 | 5200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-07-01 | 07 | SA | 168.2 | 350 | 600 | 600 | 13900 | 3200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-07-01 | 07 | RA | 108.863389603607 | 300 | 500 | 500 | 14400 | 1400 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-03-01 | 03 | SA | 147.6 | 325 | 600 | 600 | 18600 | 6600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-01-01 | 01 | SA | 141.3 | 300 | 600 | 600 | 18100 | 3000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
EG-09-01 | 09 | EA | 32.44444444444444 | 150 | 300 | 300 | 14200 | 7000 | Pickup height TBC | TBC
EG-09-02 | 09 | EA | 32.44444444444444 | 150 | 300 | 300 | 14200 | 5200 | Pickup height TBC | TBC
EG-03-01 | 03 | EA | 147.6 | 300 | 500 | 500 | 18900 | 5700 | Pickup height TBC | TBC
EG-01-01 | 01 | EA | TBC | TBC | 500 | 500 | 18600 | 1500 | Pickup height TBC | TBC

## Components
tag | service | basis | selection_status
VCD-S02 | Supply branch balancing damper | Room GF-02 | Proposed; OEM selection TBC
FSD-S02 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-02-01 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-02 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-03 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-04 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
RCD-R02 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R02 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-02-01 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-02 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-03 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-04 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
VCD-S04 | Supply branch balancing damper | Room GF-04 | Proposed; OEM selection TBC
FSD-S04 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-04-01 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
SD-04-02 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
SD-04-03 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
RCD-R04 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R04 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-04-01 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
RG-04-02 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
RG-04-03 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
EH-04 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S08 | Supply branch balancing damper | Room GF-08 | Proposed; OEM selection TBC
FSD-S08 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-08-01 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-02 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-03 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-04 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-05 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-06 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
RCD-R08 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R08 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-08-01 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-02 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-03 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-04 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-05 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-06 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
VCD-S05 | Supply branch balancing damper | Room GF-05 | Proposed; OEM selection TBC
FSD-S05 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-05-01 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-02 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-03 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-04 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-05 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
RCD-R05 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R05 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-05-01 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-02 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-03 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-04 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-05 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
EH-05 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S06 | Supply branch balancing damper | Room GF-06 | Proposed; OEM selection TBC
FSD-S06 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-06-01 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
SD-06-02 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
SD-06-03 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
RCD-R06 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R06 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-06-01 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-02 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-03 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-04 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
EH-06 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S09 | Supply branch balancing damper | Room GF-09 | Proposed; OEM selection TBC
FSD-S09 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-09-01 | Supply diffuser with integral OBD | Room GF-09; 23.100 L/s | Proposed; OEM selection TBC
SD-09-02 | Supply diffuser with integral OBD | Room GF-09; 23.100 L/s | Proposed; OEM selection TBC
VCD-S07 | Supply branch balancing damper | Room GF-07 | Proposed; OEM selection TBC
FSD-S07 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-07-01 | Supply diffuser with integral OBD | Room GF-07; 168.200 L/s | Proposed; OEM selection TBC
RCD-R07 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R07 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-07-01 | Ducted return grille with OBD | Room GF-07; 108.863 L/s | Proposed; OEM selection TBC
EH-07 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S03 | Supply branch balancing damper | Room GF-03 | Proposed; OEM selection TBC
FSD-S03 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-03-01 | Supply diffuser with integral OBD | Room GF-03; 147.600 L/s | Proposed; OEM selection TBC
EH-03 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S01 | Supply branch balancing damper | Room GF-01 | Proposed; OEM selection TBC
FSD-S01 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-01-01 | Supply diffuser with integral OBD | Room GF-01; 141.300 L/s | Proposed; OEM selection TBC
EG-09-01 | Dedicated extract grille | GF-09; final pickup height / model TBC | Proposed; OEM selection TBC
EG-09-02 | Dedicated extract grille | GF-09; final pickup height / model TBC | Proposed; OEM selection TBC
MD-IE09-01 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-09-01 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E09-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
MD-IE09-02 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-09-02 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E09-02 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
EG-03-01 | Dedicated extract grille | GF-03; final pickup height / model TBC | Proposed; OEM selection TBC
MD-IE03-01 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-03-01 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E03-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
MD-IE03-02 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-03-02 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E03-02 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
EG-01-01 | Dedicated extract grille | GF-01; final pickup height / model TBC | Proposed; OEM selection TBC
EF-01-01 | Clean-agent extract fan | One fan shown; quantity / agent suitability TBC | Proposed; OEM selection TBC
MD-E01-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
HPCP-01 | Dedicated PLC HVAC power and control panel | 15.1 / 15.10 / 15.11; 20% spare I/O and CPU; separate duty / standby modules | Proposed; OEM selection TBC
HMI-01 | Local colour touchscreen HMI, >=10 inch | 15.12.1; alarms, trends, security, operating hours and energy | Proposed; OEM selection TBC
BMS-IF-01 | BMS / SCADA interface and operator workstation | 8.5.1 / 8.5.2; protocol and point mapping TBC | Proposed; OEM selection TBC
STL-01 | Outdoor sand trap louver / bird mesh | 7.12.1 / 7.7.1; mesh <=13 mm; SS316L when within 5 km of sea | Proposed; OEM selection TBC
F-OA-01 | Washable MERV 8 outdoor intake filter | 7.12.1; clean / dirty loss and face area TBC | Proposed; OEM selection TBC
OA-SIL-01 | Common outdoor intake sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
EA-SIL-03 | Dedicated extract sound attenuator | GF-03; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
EA-SIL-09 | Dedicated extract sound attenuator | GF-09; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
EA-SIL-01 | Dedicated extract sound attenuator | GF-01; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
STL-B1 | Cable basement sand trap louver / bird mesh | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
F-OA-B1 | Basement intake MERV 8 filter | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
OA-SIL-B1 | Basement intake sound attenuator | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
EA-SIL-B1-01 | Basement extract sound attenuator 1 | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
EA-SIL-B1-02 | Basement extract sound attenuator 2 | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
MD-OA-01 | Common outdoor-air modulating damper | Proposed minimum OA / building pressure control; final OA TBC | Proposed; OEM selection TBC
PRD-01 | Common outdoor relief path and relief control | 7.13 / user relief basis; Qrelief = QOA - 691.12 only under current assumed RA | Proposed; OEM selection TBC
SA-SIL-01 | Common supply sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
RA-SIL-01 | Common return sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
EH-COM-01 | Common electric duct heater in proposed weather-protected roof enclosure | 7.8.2; heating load / high-limit / airflow proof TBC | Rev11 roof option; OEM weather suitability / enclosure / safety / duty TBC
HUM-01 | Steam humidifier in main supply, if required | 7.10.1; conditional requirement / duty TBC | Rev11 proposed weather-protected roof plant; conditional duty / mounting / maintenance access TBC
PAU-A | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-A | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-A | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-A | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-A | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-A | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-A | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
PAU-B | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-B | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-B | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-B | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-B | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-B | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-B | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
PAU-C | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-C | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-C | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-C | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-C | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-C | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-C | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
SF-B1-01 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-SF-B1-01 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-ISF-B1-01 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
SF-B1-02 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-SF-B1-02 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-ISF-B1-02 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
EF-B1-01 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-EF-B1-01 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-IEF-B1-01 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
EF-B1-02 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-EF-B1-02 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-IEF-B1-02 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
AD-S02 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 02 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S08 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 08 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S09 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 09 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S03 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 03 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S01 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 01 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R02 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 02 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R08 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 08 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H03 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 03 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-HCOM-01 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater COM-01 | Rev11 proposed weather-protected roof plant; conditional duty / mounting / maintenance access TBC

## Device_locations
tag | service | room | x_mm | y_mm | rotation_deg | symbol_actuator_side | status
VCD-S02 | SA | 02 | 3900.0 | 16600.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S02 | SA | 02 | 3900.0 | 16350.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S02 | SA | 02 | 4040.0 | 16600.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
RCD-R02 | RA | 02 | 6000.0 | 18680.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-R02 | RA | 02 | 5675.0 | 18680.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-R02 | RA | 02 | 6000.0 | 18540.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S05 | SA | 05 | 12800.0 | 12800.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S05 | SA | 05 | 12800.0 | 12500.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S05 | SA | 05 | 13000.0 | 12800.0 | -0.0 | opposite | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
EH-05 | SA | 05 | 13240.0 | 12800.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-H05 | SA | 05 | 13240.0 | 12500.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
RCD-R05 | RA | 05 | 19500.0 | 11350.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-R05 | RA | 05 | 19150.0 | 11350.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-R05 | RA | 05 | 19500.0 | 11150.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S04 | SA | 04 | 3860.0 | 6500.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S04 | SA | 04 | 3860.0 | 6675.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S04 | SA | 04 | 3660.0 | 6500.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
EH-04 | SA | 04 | 3420.0 | 6500.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-H04 | SA | 04 | 3420.0 | 6675.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
RCD-R04 | RA | 04 | 4800.0 | 7430.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-R04 | RA | 04 | 5050.0 | 7430.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-R04 | RA | 04 | 4800.0 | 7570.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S08 | SA | 08 | 9460.0 | 5600.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S08 | SA | 08 | 9460.0 | 5900.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S08 | SA | 08 | 9260.0 | 5600.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
RCD-R08 | RA | 08 | 9400.0 | 7890.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-R08 | RA | 08 | 9825.0 | 7890.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-R08 | RA | 08 | 9400.0 | 8030.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S06 | SA | 06 | 12500.0 | 9745.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S06 | SA | 06 | 12725.0 | 9745.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S06 | SA | 06 | 12500.0 | 9945.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
EH-06 | SA | 06 | 12500.0 | 10185.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-H06 | SA | 06 | 12725.0 | 10185.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
RCD-R06 | RA | 06 | 11300.0 | 9150.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-R06 | RA | 06 | 11550.0 | 9150.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-R06 | RA | 06 | 11300.0 | 9290.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S07 | SA | 07 | 15500.0 | 4760.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S07 | SA | 07 | 15350.0 | 4760.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S07 | SA | 07 | 15500.0 | 4560.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
EH-07 | SA | 07 | 15500.0 | 4320.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-H07 | SA | 07 | 15350.0 | 4320.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
RCD-R07 | RA | 07 | 13000.0 | 2250.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-R07 | RA | 07 | 13175.0 | 2250.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-R07 | RA | 07 | 13000.0 | 2450.0 | 90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S09 | SA | 09 | 13400.0 | 7960.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S09 | SA | 09 | 13300.0 | 7960.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S09 | SA | 09 | 13400.0 | 7760.0 | -90.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S03 | SA | 03 | 17240.0 | 7000.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S03 | SA | 03 | 17240.0 | 6850.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S03 | SA | 03 | 17440.0 | 7000.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
EH-03 | SA | 03 | 17680.0 | 7000.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-H03 | SA | 03 | 17680.0 | 6850.0 | -0.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
VCD-S01 | SA | 01 | 19160.0 | 3500.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-S01 | SA | 01 | 19160.0 | 3650.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
FSD-S01 | SA | 01 | 18960.0 | 3500.0 | -180.0 | default | Proposed indoor bare BOD +3.400 m; access envelope / OEM clearance TBC
AD-HCOM-01 | SA | COM | TBC | TBC | TBC | TBC | Proposed roof common heater access, D-008 functional only; roof coordinates / weather enclosure / OEM clearance TBC

## Probe_locations
tag | section | zone | drawing | status
FIT-SA-01 | SA-M01 | ROOF_PROPOSAL | D-012 | Functional common-duct attachment; actual roof coordinates / straight run / insertion / weather protection TBC
TT-SA-01 | SA-M01 | ROOF_PROPOSAL | D-012 | Functional common-duct attachment; actual roof coordinates / straight run / insertion / weather protection TBC
FIT-RA-01 | RA-M01 | ROOF_PROPOSAL | D-012 | Functional common-duct attachment; actual roof coordinates / straight run / insertion / weather protection TBC
TT-RA-01 | RA-M01 | ROOF_PROPOSAL | D-012 | Functional common-duct attachment; actual roof coordinates / straight run / insertion / weather protection TBC
RHT-RA-01 | RA-M01 | ROOF_PROPOSAL | D-012 | Functional common-duct attachment; actual roof coordinates / straight run / insertion / weather protection TBC

## Instruments
tag | parameter | location | io | basis | provision | action
TT-GF-02 | Dry bulb temperature | GF-02 Electrical panel | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-02 | Relative humidity | GF-02 Electrical panel | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-02 | Room pressure vs outdoor | GF-02 Electrical panel | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-04 | Dry bulb temperature | GF-04 Meeting | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-04 | Relative humidity | GF-04 Meeting | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-04 | Room pressure vs outdoor | GF-04 Meeting | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-04 | Heater high temperature limit | EH-04 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-08 | Dry bulb temperature | GF-08 Telecom panel | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-08 | Relative humidity | GF-08 Telecom panel | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-08 | Room pressure vs outdoor | GF-08 Telecom panel | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-05 | Dry bulb temperature | GF-05 Operator console | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-05 | Relative humidity | GF-05 Operator console | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-05 | Room pressure vs outdoor | GF-05 Operator console | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-05 | Heater high temperature limit | EH-05 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-06 | Dry bulb temperature | GF-06 Reception / corridor | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-06 | Relative humidity | GF-06 Reception / corridor | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-06 | Room pressure vs outdoor | GF-06 Reception / corridor | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Required | Monitor / alarm; final range and limits TBC
TSHH-EH-06 | Heater high temperature limit | EH-06 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-09 | Dry bulb temperature | GF-09 Toilet group: two cubicles | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-09 | Relative humidity | GF-09 Toilet group: two cubicles | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-09 | Room pressure vs outdoor | GF-09 Toilet group: two cubicles | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-07 | Dry bulb temperature | GF-07 Bedroom / Resting Room | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-07 | Relative humidity | GF-07 Bedroom / Resting Room | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-07 | Room pressure vs outdoor | GF-07 Bedroom / Resting Room | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-07 | Heater high temperature limit | EH-07 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-03 | Dry bulb temperature | GF-03 Kitchen / kitchenette | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-03 | Relative humidity | GF-03 Kitchen / kitchenette | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-03 | Room pressure vs outdoor | GF-03 Kitchen / kitchenette | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-03 | Heater high temperature limit | EH-03 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-01 | Dry bulb temperature | GF-01 Clean-agent cylinder room | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-01 | Relative humidity | GF-01 Clean-agent cylinder room | AI | 8.4.1 humidity provision | Additional proposal | Monitor / alarm; final range and limits TBC
DPT-GF-01 | Room pressure vs outdoor | GF-01 Clean-agent cylinder room | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-SA-01 | Supply air temperature | Common supply | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
TT-RA-01 | Return air temperature | Common return | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
RHT-RA-01 | Return relative humidity | Common return | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
FIT-SA-01 | Common supply airflow | Common supply straight length per manufacturer | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
FIT-RA-01 | Common return airflow | Common return straight length per manufacturer | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
PDT-OA-01 | Outdoor intake filter differential pressure | F-OA-01 | AI | Additional intake filter monitoring | Additional proposal | Monitor / alarm; final range and limits TBC
PDI-OA-01 | Local intake filter differential pressure gauge | F-OA-01 | LOCAL | Additional intake filter monitoring | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-COM-01 | Common heater high-limit | EH-COM-01 | DI | Proposed OEM heater safety | OEM safety provision | Trip common heater; reset per OEM
PDT-F1-A | Filter differential pressure | PAU-A filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-A | Local filter differential pressure gauge | PAU-A filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-A | Filter differential pressure | PAU-A filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-A | Local filter differential pressure gauge | PAU-A filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-A | Evaporator fan differential pressure | PAU-A fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-A | RMS vibration velocity | PAU-A frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
PDT-F1-B | Filter differential pressure | PAU-B filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-B | Local filter differential pressure gauge | PAU-B filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-B | Filter differential pressure | PAU-B filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-B | Local filter differential pressure gauge | PAU-B filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-B | Evaporator fan differential pressure | PAU-B fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-B | RMS vibration velocity | PAU-B frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
PDT-F1-C | Filter differential pressure | PAU-C filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-C | Local filter differential pressure gauge | PAU-C filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-C | Filter differential pressure | PAU-C filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-C | Local filter differential pressure gauge | PAU-C filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-C | Evaporator fan differential pressure | PAU-C fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-C | RMS vibration velocity | PAU-C frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-03-01 | Extract fan pressure proof | EF-03-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-03-01 | RMS vibration velocity | EF-03-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-03-02 | Extract fan pressure proof | EF-03-02 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-03-02 | RMS vibration velocity | EF-03-02 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-09-01 | Extract fan pressure proof | EF-09-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-09-01 | RMS vibration velocity | EF-09-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-09-02 | Extract fan pressure proof | EF-09-02 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-09-02 | RMS vibration velocity | EF-09-02 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-01-01 | Extract fan pressure proof | EF-01-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-01-01 | RMS vibration velocity | EF-01-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-SF-B1-01 | Fan pressure proof | SF-B1-01 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-SF-B1-01 | RMS vibration velocity | SF-B1-01 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-SF-B1-02 | Fan pressure proof | SF-B1-02 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-SF-B1-02 | RMS vibration velocity | SF-B1-02 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-EF-B1-01 | Fan pressure proof | EF-B1-01 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-EF-B1-01 | RMS vibration velocity | EF-B1-01 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-EF-B1-02 | Fan pressure proof | EF-B1-02 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-EF-B1-02 | RMS vibration velocity | EF-B1-02 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
TT-B1-01 | Cable basement air temperature | Cable basement | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-B1-01 | Basement pressure vs outdoor | Cable basement | AI | Additional coordination provision | Additional proposal | Monitor / alarm; final range and limits TBC
EM-HPCP-01 | Energy metering: V, I, kW, kWh, PF, Hz; THD for VFD | HPCP feeders >7.5 kW | COMM | 8.4.1 | Required where threshold met | Power ratings / feeder quantity / protocol TBC
AFS-EH-04 | Airflow proving switch for heater safety permissive | Electric heater EH-04 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-05 | Airflow proving switch for heater safety permissive | Electric heater EH-05 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-06 | Airflow proving switch for heater safety permissive | Electric heater EH-06 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-07 | Airflow proving switch for heater safety permissive | Electric heater EH-07 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-03 | Airflow proving switch for heater safety permissive | Electric heater EH-03 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-COM-01 | Airflow proving switch for heater safety permissive | Electric heater EH-COM-01 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active

## IO_points
tag | type | signal | action | basis | status
TT-GF-02 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-02 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-02 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-04 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-04 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-04 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-04 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-08 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-08 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-08 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-05 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-05 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-05 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-05 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-06 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-06 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-06 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-06 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-09 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-09 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-09 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-07 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-07 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-07 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-07 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-03 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-03 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-03 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-03 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-01 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-01 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-01 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-SA-01 | AI | Supply air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
TT-RA-01 | AI | Return air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
RHT-RA-01 | AI | Return relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
FIT-SA-01 | AI | Common supply airflow | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
FIT-RA-01 | AI | Common return airflow | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
PDT-OA-01 | AI | Outdoor intake filter differential pressure | Monitor / alarm; final range and limits TBC | Additional intake filter monitoring | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-COM-01 | DI | Common heater high-limit | Trip common heater; reset per OEM | Proposed OEM heater safety | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-A | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-A | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-A | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-A | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-B | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-B | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-B | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-C | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-C | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-C | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-C | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-03-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-03-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-03-02 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-03-02 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-09-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-09-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-09-02 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-09-02 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-01-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-01-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B1-01 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-SF-B1-01 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B1-02 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-SF-B1-02 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-B1-01 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-EF-B1-01 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-B1-02 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-EF-B1-02 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
TT-B1-01 | AI | Cable basement air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-B1-01 | AI | Basement pressure vs outdoor | Monitor / alarm; final range and limits TBC | Additional coordination provision | Draft point allocation; safety integrity / module allocation TBC
EM-HPCP-01 | COMM | Energy metering: V, I, kW, kWh, PF, Hz; THD for VFD | Power ratings / feeder quantity / protocol TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
EH-04-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-04-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-05-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-05-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-06-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-06-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-07-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-07-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-03-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-03-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-COM-01-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-COM-01-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
FACP-FIRE-01 | DI | Confirmed fire from FACP | Stop entire HVAC; latch fire ESD | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
HPCP-ESTOP-01 | DI | Panel emergency stop | Stop / isolate per approved ESD | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
RESET-01 | DI | Local manual reset | Only after fire signal / fault clears | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
BMS-START-01 | COMM | Initial start | Normal permissives apply | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
BMS-ESD-01 | COMM | Remote emergency stop | Stop HVAC; approved mapping TBC | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
AFS-EH-04 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-05 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-06 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-07 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-03 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-COM-01 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending

## Cause_effect
trigger | input | equipment_action | damper_action | restart | basis
Confirmed fire | FACP -> HPCP | STOP all PAUs, extract and basement fans; heaters off | Damper fire positions per approved cause-and-effect; not inferred | Local manual reset after fire clears | 8.2.1 / 15.11.11
Normal start | HMI / BMS start + Auto | Prove duty path dampers; start chosen duty pair and duty extract fans | Standby PAU and parallel fan inlet / outlet paths isolated | Sequence / delays by approved OEM logic | 7.14 / 15.10.1
Duty PAU fault | Unit fault / fan DP | Alarm; isolate failed unit; enable available alternate | Maintain two healthy 50% units when available | Automatic fault changeover; minimum-runtime delay TBC | 7.20.3 / 15.10.1
Low / high room pressure | Room DPT | Proposed RCD / OA or extract-speed adjustment within airflow constraints | Respect cooling, fresh-air and minimum ACH limits | Alarm if targets cannot be met; revise supply / balance | 7.13.2 / 15.10.1
Extract duty fan fault | Fan fault / proof | Start standby for kitchen / toilet / basement | Prove available path; isolate failed path | CAG standby arrangement TBC | 7.19.1 / 7.18.3
Heater high limit / no flow | TSHH / AFS | Heater OFF by OEM hardwired safety; alarm / proof status to PLC | Fans / dampers per OEM sequence; fire overrides | Manual or OEM reset only after fault clears | Proposed OEM protection
Power loss / return | Mains / feeder status | HVAC stops; normal restart on restored power | Fire ESD latch overrides automatic restart | Automatic power-return restart only without fire latch | 15.11.9 / 10 / 11
Post-fire purge | Separate approved command | Not enabled by this drawing | Agent, fire fan suitability and makeup to be approved | No automatic purge assumed | C-H-SS-001 1.5; C-FF-SS-004 required

## Rev08_corrections
comment | correction | drawing | verification
Missing outside walls at connected duct joints | Use the exterior of locally joined section polygons; preserve shared external walls and remove only internal seams | D-001 to D-006 | Connected-envelope line coverage and rendered close-ups
Return branch / its dampers shown without continuous duct walls | GF-02 return header moved to x=6000; straight room branch to main at y=16400. RG-02-01/02 moved 200 mm to y=17000 for graphic / duct separation. Relocate RCD-R02, FSD-R02 and AD-R02 onto this straight | D-003 / D-004; Device_locations / Terminals | Proposed room geometry; device footprint contained in branch; route / grille coordinates registered
Instrument / component graphics not at the correct duct position | Check all branch device centres, access sides and rotation against the associated branch profile; connect off-duct temperature / humidity bubbles to their duct probes | D-004 to D-007; Device_locations / Instrument_locations | Geometric attachment checks and visual review

## Instrument_drawing_index
tag | io | location | provision | drawings
TT-GF-02 | AI | GF-02 Electrical panel | Required | 007
RHT-GF-02 | AI | GF-02 Electrical panel | Required | 007
DPT-GF-02 | AI | GF-02 Electrical panel | Additional proposal | 007
TT-GF-04 | AI | GF-04 Meeting | Required | 007
RHT-GF-04 | AI | GF-04 Meeting | Required | 007
DPT-GF-04 | AI | GF-04 Meeting | Additional proposal | 007
TSHH-EH-04 | DI | EH-04 | OEM safety provision | 014
TT-GF-08 | AI | GF-08 Telecom panel | Required | 007
RHT-GF-08 | AI | GF-08 Telecom panel | Required | 007
DPT-GF-08 | AI | GF-08 Telecom panel | Additional proposal | 007
TT-GF-05 | AI | GF-05 Operator console | Required | 007
RHT-GF-05 | AI | GF-05 Operator console | Required | 007
DPT-GF-05 | AI | GF-05 Operator console | Additional proposal | 007
TSHH-EH-05 | DI | EH-05 | OEM safety provision | 014
TT-GF-06 | AI | GF-06 Reception / corridor | Required | 007
RHT-GF-06 | AI | GF-06 Reception / corridor | Required | 007
DPT-GF-06 | AI | GF-06 Reception / corridor | Required | 007
TSHH-EH-06 | DI | EH-06 | OEM safety provision | 014
TT-GF-09 | AI | GF-09 Toilet group: two cubicles | Required | 007
RHT-GF-09 | AI | GF-09 Toilet group: two cubicles | Required | 007
DPT-GF-09 | AI | GF-09 Toilet group: two cubicles | Additional proposal | 007
TT-GF-07 | AI | GF-07 Bedroom / Resting Room | Required | 007
RHT-GF-07 | AI | GF-07 Bedroom / Resting Room | Required | 007
DPT-GF-07 | AI | GF-07 Bedroom / Resting Room | Additional proposal | 007
TSHH-EH-07 | DI | EH-07 | OEM safety provision | 014
TT-GF-03 | AI | GF-03 Kitchen / kitchenette | Required | 007
RHT-GF-03 | AI | GF-03 Kitchen / kitchenette | Required | 007
DPT-GF-03 | AI | GF-03 Kitchen / kitchenette | Additional proposal | 007
TSHH-EH-03 | DI | EH-03 | OEM safety provision | 014
TT-GF-01 | AI | GF-01 Clean-agent cylinder room | Required | 007
RHT-GF-01 | AI | GF-01 Clean-agent cylinder room | Additional proposal | 007
DPT-GF-01 | AI | GF-01 Clean-agent cylinder room | Additional proposal | 007
TT-SA-01 | AI | Common supply | Required | 008 / 012
TT-RA-01 | AI | Common return | Required | 008 / 012
RHT-RA-01 | AI | Common return | Required | 008 / 012
FIT-SA-01 | AI | Common supply straight length per manufacturer | Required | 008 / 012
FIT-RA-01 | AI | Common return straight length per manufacturer | Required | 008 / 012
PDT-OA-01 | AI | F-OA-01 | Additional proposal | 012
PDI-OA-01 | LOCAL | F-OA-01 | Additional proposal | 012
TSHH-EH-COM-01 | DI | EH-COM-01 | OEM safety provision | 014
PDT-F1-A | AI | PAU-A filter 1 | Required | 012
PDI-F1-A | LOCAL | PAU-A filter 1 | Required | 012
PDT-F2-A | AI | PAU-A filter 2 | Required | 012
PDI-F2-A | LOCAL | PAU-A filter 2 | Required | 012
DPT-SF-A | AI | PAU-A fan | Required | 012
VS-PAU-A | AI | PAU-A frame / fan bearing | Required | 012
PDT-F1-B | AI | PAU-B filter 1 | Required | 012
PDI-F1-B | LOCAL | PAU-B filter 1 | Required | 012
PDT-F2-B | AI | PAU-B filter 2 | Required | 012
PDI-F2-B | LOCAL | PAU-B filter 2 | Required | 012
DPT-SF-B | AI | PAU-B fan | Required | 012
VS-PAU-B | AI | PAU-B frame / fan bearing | Required | 012
PDT-F1-C | AI | PAU-C filter 1 | Required | 012
PDI-F1-C | LOCAL | PAU-C filter 1 | Required | 012
PDT-F2-C | AI | PAU-C filter 2 | Required | 012
PDI-F2-C | LOCAL | PAU-C filter 2 | Required | 012
DPT-SF-C | AI | PAU-C fan | Required | 012
VS-PAU-C | AI | PAU-C frame / fan bearing | Required | 012
DPT-EF-03-01 | AI | EF-03-01 | Additional proposal | 013
VS-EF-03-01 | AI | EF-03-01 | Required | 013
DPT-EF-03-02 | AI | EF-03-02 | Additional proposal | 013
VS-EF-03-02 | AI | EF-03-02 | Required | 013
DPT-EF-09-01 | AI | EF-09-01 | Additional proposal | 013
VS-EF-09-01 | AI | EF-09-01 | Required | 013
DPT-EF-09-02 | AI | EF-09-02 | Additional proposal | 013
VS-EF-09-02 | AI | EF-09-02 | Required | 013
DPT-EF-01-01 | AI | EF-01-01 | Additional proposal | 013
VS-EF-01-01 | AI | EF-01-01 | Required | 013
DPT-SF-B1-01 | AI | SF-B1-01 | Additional proposal | 013
VS-SF-B1-01 | AI | SF-B1-01 | Required | 013
DPT-SF-B1-02 | AI | SF-B1-02 | Additional proposal | 013
VS-SF-B1-02 | AI | SF-B1-02 | Required | 013
DPT-EF-B1-01 | AI | EF-B1-01 | Additional proposal | 013
VS-EF-B1-01 | AI | EF-B1-01 | Required | 013
DPT-EF-B1-02 | AI | EF-B1-02 | Additional proposal | 013
VS-EF-B1-02 | AI | EF-B1-02 | Required | 013
TT-B1-01 | AI | Cable basement | Required | 015
DPT-B1-01 | AI | Cable basement | Additional proposal | 015
EM-HPCP-01 | COMM | HPCP feeders >7.5 kW | Required where threshold met | 015
AFS-EH-04 | DI | Electric heater EH-04 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-05 | DI | Electric heater EH-05 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-06 | DI | Electric heater EH-06 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-07 | DI | Electric heater EH-07 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-03 | DI | Electric heater EH-03 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-COM-01 | DI | Electric heater EH-COM-01 | Proposed; OEM proof technology / setpoint TBC | 014

## Rev11_route_changes
tag | previous_points_mm | revised_points_mm | status
SA-B02 | [[1800, 16600], [4800, 16600]] | [[3600, 16600], [4800, 16600]] | Indoor roof-drop proposal
SA-H02-U01 | [[4800, 16600], [4800, 18000]] | [[4800, 16600], [4800, 17700]] | Indoor roof-drop proposal
SA-R02-01 | [[4800, 18000], [2700, 18000]] | [[4800, 17700], [2700, 17700]] | Indoor roof-drop proposal
SA-R02-02 | [[4800, 18000], [7100, 18000]] | [[4800, 17700], [7100, 17700]] | Indoor roof-drop proposal
RA-B02 | [[6000, 15500], [3500, 15500]] | [[6000, 19100], [6000, 18150]] | Indoor roof-drop proposal
RA-H02-U01 | [[6000, 17000], [6000, 15500]] | [[1500, 17000], [1500, 19100]] | Indoor roof-drop proposal
RA-H02-D01 | [[6000, 11900], [6000, 15500]] | [[1500, 11900], [1500, 17000]] | Indoor roof-drop proposal
RA-R02-01 | [[5400, 17000], [6000, 17000]] | [[2000, 17000], [1500, 17000]] | Indoor roof-drop proposal
RA-R02-02 | [[7700, 17000], [6000, 17000]] | [[7700, 17000], [8050, 17000]] | Indoor roof-drop proposal
RA-R02-03 | [[5400, 11900], [6000, 11900]] | [[2000, 11900], [1500, 11900]] | Indoor roof-drop proposal
RA-R02-04 | [[7700, 11900], [6000, 11900]] | [[7700, 11900], [8050, 11900]] | Indoor roof-drop proposal
SA-B04 | [[4150, 9475], [4150, 6500], [2900, 6500]] | [[4200, 6500], [2900, 6500]] | Indoor roof-drop proposal
RA-B04 | [[4800, 7300], [4800, 8225]] | [[4800, 7300], [4800, 8250]] | Indoor roof-drop proposal
SA-B08 | [[5700, 9475], [5700, 5600], [8500, 5600]] | [[9800, 5600], [8500, 5600]] | Indoor roof-drop proposal
SA-R08-01 | [[8500, 6500], [6500, 6500]] | [[8500, 6500], [6800, 6500]] | Indoor roof-drop proposal
SA-R08-03 | [[8500, 4200], [6500, 4200]] | [[8500, 4200], [6800, 4200]] | Indoor roof-drop proposal
SA-R08-05 | [[8500, 1700], [6500, 1700]] | [[8500, 1700], [6800, 1700]] | Indoor roof-drop proposal
RA-B08 | [[11250, 7650], [8000, 7650], [8000, 8225]] | [[9400, 7500], [9400, 8450]] | Indoor roof-drop proposal
RA-H08-U01 | [[11250, 7150], [11250, 7650]] | [[5800, 7150], [5800, 7500]] | Indoor roof-drop proposal
RA-H08-D01 | [[11250, 4600], [11250, 7150]] | [[5800, 4600], [5800, 7150]] | Indoor roof-drop proposal
RA-H08-D02 | [[11250, 900], [11250, 4600]] | [[5800, 900], [5800, 4600]] | Indoor roof-drop proposal
RA-R08-01 | [[6400, 7150], [11250, 7150]] | [[5500, 7150], [5800, 7150]] | Indoor roof-drop proposal
RA-R08-02 | [[11500, 7150], [11250, 7150]] | [[11400, 7150], [11500, 7150]] | Indoor roof-drop proposal
RA-R08-03 | [[5900, 4600], [11250, 4600]] | [[5500, 4600], [5800, 4600]] | Indoor roof-drop proposal
RA-R08-04 | [[11500, 4600], [11250, 4600]] | [[11400, 4600], [11500, 4600]] | Indoor roof-drop proposal
RA-R08-05 | [[5900, 900], [11250, 900]] | [[5500, 900], [5800, 900]] | Indoor roof-drop proposal
RA-R08-06 | [[11500, 900], [11250, 900]] | [[11400, 900], [11500, 900]] | Indoor roof-drop proposal
SA-B05 | [[1800, 12525], [14000, 12525], [14000, 13200]] | [[12500, 12800], [14000, 12800], [14000, 13200]] | Indoor roof-drop proposal
RA-B05 | [[19500, 11400], [3500, 11400]] | [[19500, 11400], [19500, 10400]] | Indoor roof-drop proposal
RA-B06 | [[11300, 8850], [11300, 8225]] | [[11300, 8850], [11300, 9800]] | Indoor roof-drop proposal
SA-B09 | [[13400, 9475], [13400, 7600]] | [[13400, 8200], [13400, 7600]] | Indoor roof-drop proposal
SA-B07 | [[15500, 9475], [15500, 3600], [14100, 3600]] | [[15500, 5000], [15500, 3600], [14100, 3600]] | Indoor roof-drop proposal
RA-B07 | [[13000, 2200], [13000, 8225]] | [[13000, 2200], [13000, 5000]] | Indoor roof-drop proposal
SA-B03 | [[17800, 9475], [17800, 7300], [18200, 7300]] | [[17000, 7000], [18200, 7000]] | Indoor roof-drop proposal
SA-H03-D01 | [[18200, 7300], [18200, 6600]] | [[18200, 7000], [18200, 6600]] | Indoor roof-drop proposal
SA-B01 | [[19400, 9475], [19400, 3500], [16800, 3500]] | [[19400, 3500], [16800, 3500]] | Indoor roof-drop proposal
RA-H02-E01 | NEW | [[8050, 11900], [8050, 17000]] | Indoor roof-drop proposal
RA-H02-E02 | NEW | [[8050, 17000], [8050, 19100]] | Indoor roof-drop proposal
RA-H02-N01 | NEW | [[1500, 19100], [6000, 19100]] | Indoor roof-drop proposal
RA-H02-N02 | NEW | [[8050, 19100], [6000, 19100]] | Indoor roof-drop proposal
RA-H08-E01 | NEW | [[11500, 900], [11500, 4600]] | Indoor roof-drop proposal
RA-H08-E02 | NEW | [[11500, 4600], [11500, 7150]] | Indoor roof-drop proposal
RA-H08-E03 | NEW | [[11500, 7150], [11500, 7500]] | Indoor roof-drop proposal
RA-H08-N01 | NEW | [[5800, 7500], [9400, 7500]] | Indoor roof-drop proposal
RA-H08-N02 | NEW | [[11500, 7500], [9400, 7500]] | Indoor roof-drop proposal

## Rev11_terminal_changes
tag | old_x_mm | old_y_mm | new_x_mm | new_y_mm | flow_l_s | status
SD-02-01 | 2700 | 18000 | 2700 | 17700 | 166.2 | Proposed; reflected ceiling / throw / noise and access coordination pending
SD-02-02 | 7100 | 18000 | 7100 | 17700 | 166.2 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-02-01 | 5400 | 17000 | 2000 | 17000 | 151.36584740090174 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-02-03 | 5400 | 11900 | 2000 | 11900 | 151.36584740090174 | Proposed; reflected ceiling / throw / noise and access coordination pending
SD-08-01 | 6500 | 6500 | 6800 | 6500 | 147.43333333333334 | Proposed; reflected ceiling / throw / noise and access coordination pending
SD-08-03 | 6500 | 4200 | 6800 | 4200 | 147.43333333333334 | Proposed; reflected ceiling / throw / noise and access coordination pending
SD-08-05 | 6500 | 1700 | 6800 | 1700 | 147.43333333333334 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-08-01 | 6400 | 7150 | 5500 | 7150 | 137.54389826726785 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-08-02 | 11500 | 7150 | 11400 | 7150 | 137.54389826726785 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-08-03 | 5900 | 4600 | 5500 | 4600 | 137.54389826726785 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-08-04 | 11500 | 4600 | 11400 | 4600 | 137.54389826726785 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-08-05 | 5900 | 900 | 5500 | 900 | 137.54389826726785 | Proposed; reflected ceiling / throw / noise and access coordination pending
RG-08-06 | 11500 | 900 | 11400 | 900 | 137.54389826726785 | Proposed; reflected ceiling / throw / noise and access coordination pending

## Rev11_size_changes
tag | previous_size_mm | revised_size_mm | flow_l_s | velocity_m_s
RA-B02 | 600x400 | 650x400 | 605.46339 | 2.32871
RA-H02-U01 | 600x400 | 450x350 | 302.731695 | 1.92211
RA-H02-D01 | 600x400 | 450x350 | 151.365848 | 0.96105
RA-B08 | 500x650 | 850x400 | 825.26339 | 2.42725
RA-H08-U01 | 500x650 | 500x350 | 412.631695 | 2.3579
RA-H08-D01 | 500x650 | 500x350 | 275.087797 | 1.57193
RA-H08-D02 | 500x650 | 500x350 | 137.543898 | 0.78597
RA-B05 | 500x525 | 700x400 | 718.36339 | 2.56558
RA-H05-U01 | 500x525 | 700x400 | 574.690712 | 2.05247
RA-H05-U02 | 500x525 | 700x400 | 431.018034 | 1.53935
RA-H05-U03 | 500x525 | 700x400 | 287.345356 | 1.02623
RA-H05-D01 | 500x525 | 700x400 | 143.672678 | 0.51312
RA-B06 | 350x550 | 500x400 | 358.86339 | 1.79432
RA-H06-D01 | 350x550 | 500x400 | 179.431695 | 0.89716
RA-H05-L01 | 500x525 | 700x400 | 287.345356 | 1.02623
RA-H05-N01 | 500x525 | 700x400 | 287.345356 | 1.02623
RA-H05-E01 | 500x525 | 700x400 | 718.36339 | 2.56558
RA-H06-L01 | 350x550 | 500x400 | 89.715847 | 0.44858
RA-H06-L02 | 350x550 | 500x400 | 179.431695 | 0.89716
RA-H06-E01 | 350x550 | 500x400 | 89.715847 | 0.44858

## Crossing_register
tag | upper | lower | x_mm | y_mm | status

## Formed_junctions
air | x_mm | y_mm | radius_mm | legs
SA | 4800 | 17700 | 192.5 | SA-H02-U01 / SA-R02-01 / SA-R02-02
SA | 4800 | 13100 | 192.5 | SA-H02-D01 / SA-R02-03 / SA-R02-04
RA | 6000 | 19100 | 225 | RA-B02 / RA-H02-N01 / RA-H02-N02
RA | 1500 | 17000 | 165.0 | RA-H02-D01 / RA-H02-U01 / RA-R02-01
RA | 1500 | 19100 | 225 | RA-H02-N01 / RA-H02-U01
RA | 1500 | 11900 | 165.0 | RA-H02-D01 / RA-R02-03
RA | 8050 | 17000 | 165.0 | RA-H02-E01 / RA-H02-E02 / RA-R02-02
RA | 8050 | 11900 | 165.0 | RA-H02-E01 / RA-R02-04
SA | 2900 | 6500 | 192.5 | SA-B04 / SA-H04-D01 / SA-H04-U01
SA | 2900 | 6600 | 178.8 | SA-H04-U01 / SA-R04-01
SA | 2900 | 4300 | 178.8 | SA-H04-D01 / SA-H04-D02 / SA-R04-02
SA | 2900 | 1900 | 178.8 | SA-H04-D02 / SA-R04-03
RA | 4800 | 7200 | 165.0 | RA-H04-D01 / RA-H04-U01 / RA-R04-01
RA | 4800 | 1000 | 165.0 | RA-H04-D02 / RA-R04-03
SA | 8500 | 5600 | 225 | SA-B08 / SA-H08-D01 / SA-H08-U01
SA | 8500 | 6500 | 178.8 | SA-H08-U01 / SA-R08-01 / SA-R08-02
SA | 8500 | 1700 | 178.8 | SA-H08-D02 / SA-R08-05 / SA-R08-06
RA | 9400 | 7500 | 225 | RA-B08 / RA-H08-N01 / RA-H08-N02
RA | 5800 | 7150 | 165.0 | RA-H08-D01 / RA-H08-U01 / RA-R08-01
RA | 5800 | 7500 | 225 | RA-H08-N01 / RA-H08-U01
RA | 5800 | 4600 | 165.0 | RA-H08-D01 / RA-H08-D02 / RA-R08-03
RA | 5800 | 900 | 165.0 | RA-H08-D02 / RA-R08-05
RA | 11500 | 900 | 165.0 | RA-H08-E01 / RA-R08-06
SA | 14000 | 18100 | 178.8 | SA-H05-U03 / SA-R05-01 / SA-R05-02
RA | 19500 | 19000 | 225 | RA-H05-N01 / RA-H05-U03
RA | 9600 | 14600 | 165.0 | RA-H05-D01 / RA-R05-03
SA | 5400 | 10700 | 165.0 | SA-H06-D01 / SA-R06-01
SA | 14700 | 10700 | 165.0 | SA-H06-E01 / SA-H06-E02 / SA-R06-02
SA | 18300 | 10700 | 165.0 | SA-H06-E02 / SA-R06-03
RA | 4500 | 8850 | 165.0 | RA-H06-L01 / RA-R06-01
RA | 18300 | 8850 | 165.0 | RA-H06-E01 / RA-R06-04
SA | 13400 | 7000 | 82.5 | SA-H09-D01 / SA-H09-D02 / SA-R09-01
SA | 13400 | 5200 | 82.5 | SA-H09-D02 / SA-R09-02
SA | 14100 | 3600 | 165.0 | SA-B07 / SA-H07-D01
SA | 14100 | 3200 | 165.0 | SA-H07-D01 / SA-R07-01
RA | 13000 | 1400 | 165.0 | RA-H07-D01 / RA-R07-01
SA | 18200 | 7000 | 165.0 | SA-B03 / SA-H03-D01
SA | 18200 | 6600 | 165.0 | SA-H03-D01 / SA-R03-01
SA | 16800 | 3500 | 165.0 | SA-B01 / SA-H01-D01
SA | 16800 | 3000 | 165.0 | SA-H01-D01 / SA-R01-01
EA | 14700 | 7000 | 82.5 | EA-B09 / EA-R09-01 / EA-R09-02
RA | 9600 | 19000 | 225 | RA-H05-L01 / RA-H05-N01
RA | 8050 | 19100 | 225 | RA-H02-E02 / RA-H02-N02
RA | 11500 | 7500 | 225 | RA-H08-E03 / RA-H08-N02

## Roof_main_basis
tag | air_type | width_mm | height_mm | flow_l_s | velocity_m_s | zone | status
SA-M01 | SA | 1200 | 650 | 3697.8 | 4.74077 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M02 | SA | 1100 | 575 | 3033.0 | 4.79526 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M03 | SA | 650 | 750 | 2255.3 | 4.62626 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M04 | SA | 650 | 575 | 1806.1 | 4.83237 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M05 | SA | 650 | 300 | 921.5 | 4.72564 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M06 | SA | 500 | 250 | 503.3 | 4.0264 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M07 | SA | 450 | 250 | 457.1 | 4.06311 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M08 | SA | 400 | 200 | 288.9 | 3.61125 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
SA-M09 | SA | 300 | 200 | 141.3 | 2.355 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
RA-M01 | RA | 1400 | 650 | 3006.680338 | 3.30404 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
RA-M02 | RA | 1200 | 600 | 2401.216948 | 3.33502 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
RA-M03 | RA | 600 | 800 | 1682.853558 | 3.50594 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
RA-M04 | RA | 600 | 600 | 1292.990169 | 3.59164 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
RA-M05 | RA | 350 | 575 | 467.726779 | 2.32411 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC
RA-M06 | RA | 350 | 300 | 108.86339 | 1.03679 | ROOF_PROPOSAL | Functional flow/size basis only; actual roof route, lengths, levels, weather insulation and fitting losses TBC

## Roof_risers
tag | branch | air_type | room | x_mm | y_mm | width_mm | height_mm | flow_l_s | indoor_bod_mm_affl | roof_bod_mm_affl | vertical_length_m | status
RS-SA02 | SA-B02 | SA | 02 | 3600 | 16600 | 500 | 350 | 664.8 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-RA02 | RA-B02 | RA | 02 | 6000 | 18150 | 650 | 400 | 605.46339 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA04 | SA-B04 | SA | 04 | 4200 | 6500 | 350 | 400 | 449.2 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-RA04 | RA-B04 | RA | 04 | 4800 | 8250 | 500 | 350 | 389.86339 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA08 | SA-B08 | SA | 08 | 9800 | 5600 | 600 | 400 | 884.6 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-RA08 | RA-B08 | RA | 08 | 9400 | 8450 | 850 | 400 | 825.26339 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA05 | SA-B05 | SA | 05 | 12500 | 12800 | 600 | 350 | 777.7 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-RA05 | RA-B05 | RA | 05 | 19500 | 10400 | 700 | 400 | 718.36339 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA06 | SA-B06 | SA | 06 | 12500 | 9475 | 450 | 300 | 418.2 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-RA06 | RA-B06 | RA | 06 | 11300 | 9800 | 500 | 400 | 358.86339 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA09 | SA-B09 | SA | 09 | 13400 | 8200 | 200 | 150 | 46.2 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA07 | SA-B07 | SA | 07 | 15500 | 5000 | 300 | 250 | 168.2 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-RA07 | RA-B07 | RA | 07 | 13000 | 5000 | 350 | 250 | 108.86339 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA03 | SA-B03 | SA | 03 | 17000 | 7000 | 300 | 200 | 147.6 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending
RS-SA01 | SA-B01 | SA | 01 | 19400 | 3500 | 300 | 200 | 141.3 | 3400 | TBC | TBC | Proposed roof penetration/drop; structural approval, curb, weatherproofing, fire rating and access pending

## Headroom_register
section | air | room | bare_depth_mm | bare_bod_mm_affl | insulation_mm | lowest_insulated_mm_affl | highest_insulated_mm_affl | slab_clearance_mm | finished_ceiling_mm_affl | ceiling_clearance_mm | status
SA-B02 | SA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H02-U01 | SA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H02-D01 | SA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R02-01 | SA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R02-02 | SA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R02-03 | SA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R02-04 | SA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-B02 | RA | 02 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H02-U01 | RA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H02-D01 | RA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R02-01 | RA | 02 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R02-02 | RA | 02 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R02-03 | RA | 02 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R02-04 | RA | 02 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B04 | SA | 04 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H04-U01 | SA | 04 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H04-D01 | SA | 04 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H04-D02 | SA | 04 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R04-01 | SA | 04 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R04-02 | SA | 04 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R04-03 | SA | 04 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-B04 | RA | 04 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H04-U01 | RA | 04 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H04-D01 | RA | 04 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H04-D02 | RA | 04 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R04-01 | RA | 04 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R04-02 | RA | 04 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R04-03 | RA | 04 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B08 | SA | 08 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H08-U01 | SA | 08 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H08-D01 | SA | 08 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H08-D02 | SA | 08 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R08-01 | SA | 08 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R08-02 | SA | 08 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R08-03 | SA | 08 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R08-04 | SA | 08 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R08-05 | SA | 08 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R08-06 | SA | 08 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-B08 | RA | 08 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-U01 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-D01 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-D02 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R08-01 | RA | 08 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R08-02 | RA | 08 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R08-03 | RA | 08 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R08-04 | RA | 08 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R08-05 | RA | 08 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R08-06 | RA | 08 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B05 | SA | 05 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H05-U01 | SA | 05 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H05-U02 | SA | 05 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H05-U03 | SA | 05 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R05-01 | SA | 05 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R05-02 | SA | 05 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R05-03 | SA | 05 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R05-04 | SA | 05 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R05-05 | SA | 05 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-B05 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H05-U01 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H05-U02 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H05-U03 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H05-D01 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R05-01 | RA | 05 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R05-02 | RA | 05 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R05-03 | RA | 05 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R05-04 | RA | 05 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R05-05 | RA | 05 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B06 | SA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H06-D01 | SA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R06-01 | SA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R06-02 | SA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R06-03 | SA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-B06 | RA | 06 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H06-D01 | RA | 06 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R06-01 | RA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R06-02 | RA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R06-03 | RA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R06-04 | RA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B09 | SA | 09 | 150.0 | 3400 | 50 | 3350 | 3600.0 | 400.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H09-D01 | SA | 09 | 150.0 | 3400 | 50 | 3350 | 3600.0 | 400.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H09-D02 | SA | 09 | 150.0 | 3400 | 50 | 3350 | 3600.0 | 400.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R09-01 | SA | 09 | 150.0 | 3400 | 50 | 3350 | 3600.0 | 400.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R09-02 | SA | 09 | 150.0 | 3400 | 50 | 3350 | 3600.0 | 400.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B07 | SA | 07 | 250.0 | 3400 | 50 | 3350 | 3700.0 | 300.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H07-D01 | SA | 07 | 250.0 | 3400 | 50 | 3350 | 3700.0 | 300.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R07-01 | SA | 07 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-B07 | RA | 07 | 250.0 | 3400 | 50 | 3350 | 3700.0 | 300.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H07-D01 | RA | 07 | 250.0 | 3400 | 50 | 3350 | 3700.0 | 300.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-R07-01 | RA | 07 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B03 | SA | 03 | 200.0 | 3400 | 50 | 3350 | 3650.0 | 350.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H03-D01 | SA | 03 | 200.0 | 3400 | 50 | 3350 | 3650.0 | 350.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R03-01 | SA | 03 | 325.0 | 3400 | 50 | 3350 | 3775.0 | 225.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-B01 | SA | 01 | 200.0 | 3400 | 50 | 3350 | 3650.0 | 350.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H01-D01 | SA | 01 | 200.0 | 3400 | 50 | 3350 | 3650.0 | 350.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-R01-01 | SA | 01 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
EA-B09 | EA | 09 | 200.0 | 3400 | 50 | 3350 | 3650.0 | 350.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
EA-R09-01 | EA | 09 | 150.0 | 3400 | 50 | 3350 | 3600.0 | 400.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
EA-R09-02 | EA | 09 | 150.0 | 3400 | 50 | 3350 | 3600.0 | 400.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
EA-B03 | EA | 03 | 200.0 | 3400 | 50 | 3350 | 3650.0 | 350.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H05-L01 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H05-N01 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H05-E01 | RA | 05 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H06-E01 | SA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
SA-H06-E02 | SA | 06 | 300.0 | 3400 | 50 | 3350 | 3750.0 | 250.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H06-L01 | RA | 06 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H06-L02 | RA | 06 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H06-E01 | RA | 06 | 400.0 | 3400 | 50 | 3350 | 3850.0 | 150.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H02-E01 | RA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H02-E02 | RA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H02-N01 | RA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H02-N02 | RA | 02 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-E01 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-E02 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-E03 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-N01 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified
RA-H08-N02 | RA | 08 | 350.0 | 3400 | 50 | 3350 | 3800.0 | 200.0 | 3300 | 50 | Duct envelope fits only; actual support, flange, actuator and terminal/plenum envelope unverified

## Sizing_check
Section | Air | Room | Flow L/s | Width mm | Height mm | Diameter mm | Area m2 | Velocity m/s | Scheduled m/s | Difference m/s | Length m | Basis
SA-B02 | SA | 02 | 664.8 | 500 | 350 |  | 0.175 | 3.7989 | 3.7989 | -2.8571e-06 | 1.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H02-U01 | SA | 02 | 332.4 | 500 | 350 |  | 0.175 | 1.8994 | 1.8994 | -1.4286e-06 | 1.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H02-D01 | SA | 02 | 332.4 | 500 | 350 |  | 0.175 | 1.8994 | 1.8994 | -1.4286e-06 | 3.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R02-01 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R02-02 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R02-03 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R02-04 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-B02 | RA | 02 | 605.4634 | 650 | 400 |  | 0.26 | 2.3287 | 2.3287 | -4.6538e-06 | 0.95 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H02-U01 | RA | 02 | 302.7317 | 450 | 350 |  | 0.1575 | 1.9221 | 1.9221 | -4e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H02-D01 | RA | 02 | 151.3658 | 450 | 350 |  | 0.1575 | 0.96105 | 0.96105 | 3.0032e-06 | 5.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R02-01 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 0.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R02-02 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 0.35 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R02-03 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 0.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R02-04 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 0.35 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B04 | SA | 04 | 449.2 | 350 | 400 |  | 0.14 | 3.2086 | 3.2086 | 1.4286e-06 | 1.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H04-U01 | SA | 04 | 149.7333 | 450 | 300 |  | 0.135 | 1.1091 | 1.1091 | -4.2e-06 | 0.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H04-D01 | SA | 04 | 299.4667 | 450 | 300 |  | 0.135 | 2.2183 | 2.2183 | 1.6074e-06 | 2.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H04-D02 | SA | 04 | 149.7333 | 450 | 300 |  | 0.135 | 1.1091 | 1.1091 | -4.2e-06 | 2.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R04-01 | SA | 04 | 149.7333 | 325 |  | 325 | 0.082958 | 1.8049 | 1.8049 | -3.6616e-06 | 1.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R04-02 | SA | 04 | 149.7333 | 325 |  | 325 | 0.082958 | 1.8049 | 1.8049 | -3.6616e-06 | 1.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R04-03 | SA | 04 | 149.7333 | 325 |  | 325 | 0.082958 | 1.8049 | 1.8049 | -3.6616e-06 | 1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-B04 | RA | 04 | 389.8634 | 500 | 350 |  | 0.175 | 2.2278 | 2.2278 | 8e-07 | 0.95 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H04-U01 | RA | 04 | 389.8634 | 500 | 350 |  | 0.175 | 2.2278 | 2.2278 | 8e-07 | 0.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H04-D01 | RA | 04 | 259.9089 | 500 | 350 |  | 0.175 | 1.4852 | 1.4852 | 3.8629e-06 | 2.9 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H04-D02 | RA | 04 | 129.9545 | 500 | 350 |  | 0.175 | 0.7426 | 0.7426 | -3.0686e-06 | 3.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R04-01 | RA | 04 | 129.9545 | 300 |  | 300 | 0.070686 | 1.8385 | 1.8385 | -4.2993e-07 | 4.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R04-02 | RA | 04 | 129.9545 | 300 |  | 300 | 0.070686 | 1.8385 | 1.8385 | -4.2993e-07 | 0.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R04-03 | RA | 04 | 129.9545 | 300 |  | 300 | 0.070686 | 1.8385 | 1.8385 | -4.2993e-07 | 4.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B08 | SA | 08 | 884.6 | 600 | 400 |  | 0.24 | 3.6858 | 3.6858 | 3.3333e-06 | 1.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H08-U01 | SA | 08 | 294.8667 | 600 | 400 |  | 0.24 | 1.2286 | 1.2286 | 1.1125e-06 | 0.9 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H08-D01 | SA | 08 | 589.7333 | 600 | 400 |  | 0.24 | 2.4572 | 2.4572 | 2.2208e-06 | 1.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H08-D02 | SA | 08 | 294.8667 | 600 | 400 |  | 0.24 | 1.2286 | 1.2286 | 1.1125e-06 | 2.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R08-01 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 1.7 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R08-02 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R08-03 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 1.7 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R08-04 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R08-05 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 1.7 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R08-06 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-B08 | RA | 08 | 825.2634 | 850 | 400 |  | 0.34 | 2.4272 | 2.4272 | -4.7353e-06 | 0.95 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-U01 | RA | 08 | 412.6317 | 500 | 350 |  | 0.175 | 2.3579 | 2.3579 | -4.6e-06 | 0.35 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-D01 | RA | 08 | 275.0878 | 500 | 350 |  | 0.175 | 1.5719 | 1.5719 | 2.6857e-07 | 2.55 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-D02 | RA | 08 | 137.5439 | 500 | 350 |  | 0.175 | 0.78597 | 0.78597 | -4.8686e-06 | 3.7 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R08-01 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 0.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R08-02 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 0.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R08-03 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 0.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R08-04 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 0.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R08-05 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 0.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R08-06 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 0.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B05 | SA | 05 | 777.7 | 600 | 350 |  | 0.21 | 3.7033 | 3.7033 | 3.3333e-06 | 1.9 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H05-U01 | SA | 05 | 777.7 | 600 | 350 |  | 0.21 | 3.7033 | 3.7033 | 3.3333e-06 | 0.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H05-U02 | SA | 05 | 466.62 | 600 | 350 |  | 0.21 | 2.222 | 2.222 | 0 | 2.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H05-U03 | SA | 05 | 311.08 | 600 | 350 |  | 0.21 | 1.4813 | 1.4813 | 3.3333e-06 | 2.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R05-01 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 3.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R05-02 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 2.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R05-03 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 4.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R05-04 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 3.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R05-05 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 2.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-B05 | RA | 05 | 718.3634 | 700 | 400 |  | 0.28 | 2.5656 | 2.5656 | 3.5357e-06 | 1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H05-U01 | RA | 05 | 574.6907 | 700 | 400 |  | 0.28 | 2.0525 | 2.0525 | -3.1714e-06 | 0.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H05-U02 | RA | 05 | 431.018 | 700 | 400 |  | 0.28 | 1.5394 | 1.5393 | 1.2143e-07 | 6.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H05-U03 | RA | 05 | 287.3454 | 700 | 400 |  | 0.28 | 1.0262 | 1.0262 | 3.4143e-06 | 0.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H05-D01 | RA | 05 | 143.6727 | 700 | 400 |  | 0.28 | 0.51312 | 0.51312 | -3.2929e-06 | 4.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R05-01 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 0.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R05-02 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 0.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R05-03 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 0.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R05-04 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 0.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R05-05 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 4.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B06 | SA | 06 | 418.2 | 450 | 300 |  | 0.135 | 3.0978 | 3.0978 | -2.2222e-06 | 1.225 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H06-D01 | SA | 06 | 139.4 | 450 | 300 |  | 0.135 | 1.0326 | 1.0326 | 2.5926e-06 | 7.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R06-01 | SA | 06 | 139.4 | 300 |  | 300 | 0.070686 | 1.9721 | 1.9721 | -3.4163e-06 | 0.55 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R06-02 | SA | 06 | 139.4 | 300 |  | 300 | 0.070686 | 1.9721 | 1.9721 | -3.4163e-06 | 0.55 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R06-03 | SA | 06 | 139.4 | 300 |  | 300 | 0.070686 | 1.9721 | 1.9721 | -3.4163e-06 | 0.55 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-B06 | RA | 06 | 358.8634 | 500 | 400 |  | 0.2 | 1.7943 | 1.7943 | -3.05e-06 | 0.95 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H06-D01 | RA | 06 | 179.4317 | 500 | 400 |  | 0.2 | 0.89716 | 0.89716 | -1.525e-06 | 5.9 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R06-01 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 0.025 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R06-02 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 0.025 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R06-03 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 0.025 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R06-04 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 0.025 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B09 | SA | 09 | 46.2 | 200 | 150 |  | 0.03 | 1.54 | 1.54 | 2.2204e-16 | 0.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H09-D01 | SA | 09 | 46.2 | 200 | 150 |  | 0.03 | 1.54 | 1.54 | 2.2204e-16 | 0.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H09-D02 | SA | 09 | 23.1 | 200 | 150 |  | 0.03 | 0.77 | 0.77 | 1.1102e-16 | 1.8 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R09-01 | SA | 09 | 23.1 | 150 |  | 150 | 0.017671 | 1.3072 | 1.3072 | 2.5993e-06 | 0.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R09-02 | SA | 09 | 23.1 | 150 |  | 150 | 0.017671 | 1.3072 | 1.3072 | 2.5993e-06 | 0.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B07 | SA | 07 | 168.2 | 300 | 250 |  | 0.075 | 2.2427 | 2.2427 | -3.3333e-06 | 2.8 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H07-D01 | SA | 07 | 168.2 | 300 | 250 |  | 0.075 | 2.2427 | 2.2427 | -3.3333e-06 | 0.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R07-01 | SA | 07 | 168.2 | 350 |  | 350 | 0.096211 | 1.7482 | 1.7482 | -4.1516e-06 | 0.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-B07 | RA | 07 | 108.8634 | 350 | 250 |  | 0.0875 | 1.2442 | 1.2442 | 3.0286e-06 | 2.8 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H07-D01 | RA | 07 | 108.8634 | 350 | 250 |  | 0.0875 | 1.2442 | 1.2442 | 3.0286e-06 | 0.8 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-R07-01 | RA | 07 | 108.8634 | 300 |  | 300 | 0.070686 | 1.5401 | 1.5401 | 1.9236e-06 | 1.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B03 | SA | 03 | 147.6 | 300 | 200 |  | 0.06 | 2.46 | 2.46 | 0 | 1.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H03-D01 | SA | 03 | 147.6 | 300 | 200 |  | 0.06 | 2.46 | 2.46 | 0 | 0.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R03-01 | SA | 03 | 147.6 | 325 |  | 325 | 0.082958 | 1.7792 | 1.7792 | 4.1944e-07 | 0.4 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-B01 | SA | 01 | 141.3 | 300 | 200 |  | 0.06 | 2.355 | 2.355 | 4.4409e-16 | 2.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H01-D01 | SA | 01 | 141.3 | 300 | 200 |  | 0.06 | 2.355 | 2.355 | 4.4409e-16 | 0.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-R01-01 | SA | 01 | 141.3 | 300 |  | 300 | 0.070686 | 1.999 | 1.999 | -3.9148e-06 | 1.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
EA-B09 | EA | 09 | 64.8889 | 250 | 200 |  | 0.05 | 1.2978 | 1.2978 | -2.22e-06 | 6.7 | Rev11 proposed clear size; retained room duty; recomputed velocity
EA-R09-01 | EA | 09 | 32.4444 | 150 |  | 150 | 0.017671 | 1.836 | 1.836 | -3.9656e-08 | 0.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
EA-R09-02 | EA | 09 | 32.4444 | 150 |  | 150 | 0.017671 | 1.836 | 1.836 | -3.9656e-08 | 2.3 | Rev11 proposed clear size; retained room duty; recomputed velocity
EA-B03 | EA | 03 | 147.6 | 300 | 200 |  | 0.06 | 2.46 | 2.46 | 0 | 1.9 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H05-L01 | RA | 05 | 287.3454 | 700 | 400 |  | 0.28 | 1.0262 | 1.0262 | 3.4143e-06 | 0.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H05-N01 | RA | 05 | 287.3454 | 700 | 400 |  | 0.28 | 1.0262 | 1.0262 | 3.4143e-06 | 9.9 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H05-E01 | RA | 05 | 718.3634 | 700 | 400 |  | 0.28 | 2.5656 | 2.5656 | 3.5357e-06 | 0.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H06-E01 | SA | 06 | 278.8 | 450 | 300 |  | 0.135 | 2.0652 | 2.0652 | -4.8148e-06 | 2.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
SA-H06-E02 | SA | 06 | 139.4 | 450 | 300 |  | 0.135 | 1.0326 | 1.0326 | 2.5926e-06 | 3.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H06-L01 | RA | 06 | 89.7158 | 500 | 400 |  | 0.2 | 0.44858 | 0.44858 | -7.65e-07 | 5.2 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H06-L02 | RA | 06 | 179.4317 | 500 | 400 |  | 0.2 | 0.89716 | 0.89716 | -1.525e-06 | 1.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H06-E01 | RA | 06 | 89.7158 | 500 | 400 |  | 0.2 | 0.44858 | 0.44858 | -7.65e-07 | 1.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H02-E01 | RA | 02 | 151.3658 | 450 | 350 |  | 0.1575 | 0.96105 | 0.96105 | 3.0032e-06 | 5.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H02-E02 | RA | 02 | 302.7317 | 450 | 350 |  | 0.1575 | 1.9221 | 1.9221 | -4e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H02-N01 | RA | 02 | 302.7317 | 450 | 350 |  | 0.1575 | 1.9221 | 1.9221 | -4e-06 | 4.5 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H02-N02 | RA | 02 | 302.7317 | 450 | 350 |  | 0.1575 | 1.9221 | 1.9221 | -4e-06 | 2.05 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-E01 | RA | 08 | 137.5439 | 500 | 350 |  | 0.175 | 0.78597 | 0.78597 | -4.8686e-06 | 3.7 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-E02 | RA | 08 | 275.0878 | 500 | 350 |  | 0.175 | 1.5719 | 1.5719 | 2.6857e-07 | 2.55 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-E03 | RA | 08 | 412.6317 | 500 | 350 |  | 0.175 | 2.3579 | 2.3579 | -4.6e-06 | 0.35 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-N01 | RA | 08 | 412.6317 | 500 | 350 |  | 0.175 | 2.3579 | 2.3579 | -4.6e-06 | 3.6 | Rev11 proposed clear size; retained room duty; recomputed velocity
RA-H08-N02 | RA | 08 | 412.6317 | 500 | 350 |  | 0.175 | 2.3579 | 2.3579 | -4.6e-06 | 2.1 | Rev11 proposed clear size; retained room duty; recomputed velocity

## Comment_closure
Comment | Rev11 action | Drawing / register | Status
3.30 m clear height below 4.00 m slab | Limit indoor depth to 400 mm; propose bare BOD +3.400 m, roof common mains and separate room drops | D-020 / D-022 / Headroom_register | Duct envelope checked; Roof strategy selected; structural / OEM selections pending
Multiple duct crossings | Perimeter return trees / independent room feeds replace ceiling common mains | D-001 to D-006 / D-019 | Zero bare indoor crossings; separate-service 50 mm insulation envelopes do not overlap
Connections / controls | Continuous exterior, replacement neck adapters, actual formed junctions and serial branch devices | D-019 / Device_locations / Formed_junctions | Connected room trees / station bodies checked; fabrication and access pending
Instrumentation | Retain 85 requirements / I/O and relocate common-duct context to roof plant | D-012 to D-016 / Instrument_drawing_index | All tags referenced; roof physical mounting pending
Roof extension | Separate functional common-main basis from indoor measured paths; schedule all 15 proposed risers | Roof_main_basis / Roof_risers / D-022 | Actual roof routing, structure, weatherproofing, loads, levels and ESP not designed from survey