## Read_me
ADMINISTRATION HVAC - REV09 DRAWING REGISTERS | 07 October 2026 ¦ engineering coordination issue
Purpose | Excel companion to the revised drawings. This is a drawing register and sizing cross-check; it does not replace the earlier HAP/duct calculation workbook.
Supply basis | 3697.80 L/s total; room airflows and selected section sizes retained from Rev05.
Return basis | 3006.68 L/s assumed total; achieved pressure remains unverified.
Pressure targets | +50 Pa normal / return rooms; +25 Pa kitchen, toilets and clean-agent, relative to outdoors.
Room connections | Clean-agent, kitchen and toilets have cooled PAU supply, dedicated extract and no shared return. GF-07 is a resting/bed room with return.
Plant / fire | PAUs: 3 x 50%, rotating pair of two duty units. Confirmed fire stops all HVAC fans and heaters.
Drawing comments | See Comment_closure for the visible screenshot corrections and their drawing references.
Duct sections | One row per main, branch, header or terminal runout. Do not sum all section flows: the same air passes through several sections.
Lengths | Horizontal lengths are proposed centreline allowances. Rev08 route changes are recorded. Vertical lengths, developed fittings and elevations remain TBC.
Sizing_check | Recomputed cross-sectional area and velocity using the existing flow and section sizes. The tab does not select new sizes.
Transitions | 13 main tapers, 15 room branch boots and 49 external terminal adaptors have explicit proposed plan geometry. SD-07-01 and RG-05-05 use short direct / integral plenum conversions; see D-009 / D-011.
Access / instruments | 21 duct access doors; 85 instruments including six explicit heater airflow-proof DI inputs. OEM safety remains hardwired independently of PLC demand.
Rev08 locations | Branch device bodies checked within their ducts; AD centres checked on the duct wall. Probe_locations records five common duct instrument attachments. All positions are proposed pending levels and OEM clearances.
GF-02 route change | Return collection header moved to x=6000 mm; branch is straight at y=16400 mm. RG-02-01 and RG-02-02 move 200 mm to y=17000 mm. Runout/header lengths are synchronized; flows and neck/face sizes are retained.
I/O | 65 AI, 22 AO, 141 DI, 44 DO; three COMM interfaces. 20% spare is rounded up by signal class; module allocation remains pending.
Holds | Actual room pressure balance, outdoor-air compliance / HAP rerun, CAG and basement duties, catalogue selections, fitting K, fan ESP, levels and final control settings remain open.
Rev09 drawing detail | 18 detailed A1 sheets; 85 tagged instruments; native plan dimensions; complete instrument drawing index. Rev08 duties and section sizes retained.
How to edit | Revise the linked JSON / CSV inputs together and regenerate PDF, DXF and this workbook. The drawing source does not read edits made only in this Excel companion.

## Duct_sections
tag | air_type | role | room | flow_l_s | width_mm | height_mm | diameter_mm | velocity_m_s | friction_pa_m | horizontal_length_m | vertical_length_m | level | route_basis | points_mm
SA-M01 | SA | Main |  | 3697.8 | 1200 | 650 |  | 4.74077 | 0.25215 | 2.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[1800, 19000], [1800, 16600]]
SA-M02 | SA | Main |  | 3033.0 | 1100 | 575 |  | 4.79526 | 0.29408 | 3.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[1800, 16600], [1800, 13200]]
SA-M03 | SA | Main |  | 2255.3 | 950 | 500 |  | 4.748 | 0.3427 | 5.6 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[1800, 13200], [1800, 9300], [3500, 9300]]
SA-M04 | SA | Main |  | 1806.1 | 850 | 425 |  | 4.99958 | 0.44937 | 3.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3500, 9300], [7000, 9300]]
SA-M05 | SA | Main |  | 921.5 | 650 | 300 |  | 4.72564 | 0.59869 | 4.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[7000, 9300], [11000, 9300]]
SA-M06 | SA | Main |  | 503.3 | 500 | 250 |  | 4.0264 | 0.57488 | 2.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[11000, 9300], [13200, 9300]]
SA-M07 | SA | Main |  | 457.1 | 450 | 250 |  | 4.06311 | 0.61115 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[13200, 9300], [15500, 9300]]
SA-M08 | SA | Main |  | 288.9 | 400 | 200 |  | 3.61125 | 0.61935 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[15500, 9300], [17800, 9300]]
SA-M09 | SA | Main |  | 141.3 | 300 | 200 |  | 2.355 | 0.32451 | 0.7 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[17800, 9300], [18500, 9300]]
RA-M01 | RA | Main |  | 3006.680338 | 1400 | 650 |  | 3.30404 | 0.12169 | 2.6 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3500, 16400], [3500, 19000]]
RA-M02 | RA | Main |  | 2401.216948 | 1200 | 600 |  | 3.33502 | 0.14037 | 4.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3500, 12200], [3500, 16400]]
RA-M03 | RA | Main |  | 1682.853558 | 850 | 550 |  | 3.59969 | 0.2009 | 4.45 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4100, 8350], [3500, 8350], [3500, 12200]]
RA-M04 | RA | Main |  | 1292.990169 | 800 | 450 |  | 3.59164 | 0.23936 | 3.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[7500, 8350], [4100, 8350]]
RA-M05 | RA | Main |  | 467.726779 | 650 | 300 |  | 2.3986 | 0.17307 | 3.8 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[11300, 8350], [7500, 8350]]
RA-M06 | RA | Main |  | 108.86339 | 450 | 225 |  | 1.07519 | 0.06042 | 4.05 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[15350, 8350], [11300, 8350]]
SA-B02 | SA | Branch | 02 | 664.8 | 500 | 350 |  | 3.79886 | 0.3991 | 3.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[1800, 16600], [4800, 16600]]
SA-H02-U01 | SA | Room header | 02 | 332.4 | 500 | 350 |  | 1.89943 | 0.11304 | 1.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4800, 16600], [4800, 18000]]
SA-H02-D01 | SA | Room header | 02 | 332.4 | 500 | 350 |  | 1.89943 | 0.11304 | 3.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4800, 16600], [4800, 13100]]
SA-R02-01 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4800, 18000], [2700, 18000]]
SA-R02-02 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4800, 18000], [7100, 18000]]
SA-R02-03 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4800, 13100], [2700, 13100]]
SA-R02-04 | SA | Runout | 02 | 166.2 | 350 |  | 350 | 1.72745 | 0.1164 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4800, 13100], [7100, 13100]]
RA-B02 | RA | Branch | 02 | 605.46339 | 600 | 400 |  | 2.52276 | 0.15666 | 2.5 | TBC | BOD TBC | Rev08 proposed GF-02 return clearance route; branch no longer coincides with its collection header. Duct levels / fabrication development TBC | [[6000, 16400], [3500, 16400]]
RA-H02-U01 | RA | Room header | 02 | 302.731695 | 600 | 400 |  | 1.26138 | 0.04483 | 0.6 | TBC | BOD TBC | Rev08 proposed GF-02 return clearance route; branch no longer coincides with its collection header. Duct levels / fabrication development TBC | [[6000, 17000], [6000, 16400]]
RA-H02-D01 | RA | Room header | 02 | 302.731695 | 600 | 400 |  | 1.26138 | 0.04483 | 4.5 | TBC | BOD TBC | Rev08 proposed GF-02 return clearance route; branch no longer coincides with its collection header. Duct levels / fabrication development TBC | [[6000, 11900], [6000, 16400]]
RA-R02-01 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 4.8 | TBC | BOD TBC | Rev08 proposed GF-02 return clearance route; branch no longer coincides with its collection header. Duct levels / fabrication development TBC | [[1200, 17000], [6000, 17000]]
RA-R02-02 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 1.7 | TBC | BOD TBC | Rev08 proposed GF-02 return clearance route; branch no longer coincides with its collection header. Duct levels / fabrication development TBC | [[7700, 17000], [6000, 17000]]
RA-R02-03 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 4.8 | TBC | BOD TBC | Rev08 proposed GF-02 return clearance route; branch no longer coincides with its collection header. Duct levels / fabrication development TBC | [[1200, 11900], [6000, 11900]]
RA-R02-04 | RA | Runout | 02 | 151.365847 | 300 |  | 300 | 2.14139 | 0.20737 | 1.7 | TBC | BOD TBC | Rev08 proposed GF-02 return clearance route; branch no longer coincides with its collection header. Duct levels / fabrication development TBC | [[7700, 11900], [6000, 11900]]
SA-B04 | SA | Branch | 04 | 449.2 | 450 | 300 |  | 3.32741 | 0.36896 | 3.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3500, 9300], [3500, 6500], [2900, 6500]]
SA-H04-U01 | SA | Room header | 04 | 149.733333 | 450 | 300 |  | 1.10914 | 0.05087 | 0.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[2900, 6500], [2900, 6600]]
SA-H04-D01 | SA | Room header | 04 | 299.466667 | 450 | 300 |  | 2.21827 | 0.17652 | 2.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[2900, 6500], [2900, 4300]]
SA-H04-D02 | SA | Room header | 04 | 149.733333 | 450 | 300 |  | 1.10914 | 0.05087 | 2.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[2900, 4300], [2900, 1900]]
SA-R04-01 | SA | Runout | 04 | 149.733333 | 325 |  | 325 | 1.80494 | 0.13805 | 1.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[2900, 6600], [1800, 6600]]
SA-R04-02 | SA | Runout | 04 | 149.733333 | 325 |  | 325 | 1.80494 | 0.13805 | 1.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[2900, 4300], [4300, 4300]]
SA-R04-03 | SA | Runout | 04 | 149.733333 | 325 |  | 325 | 1.80494 | 0.13805 | 1.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[2900, 1900], [1900, 1900]]
RA-B04 | RA | Branch | 04 | 389.86339 | 500 | 350 |  | 2.22779 | 0.15082 | 2.55 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3000, 6900], [4100, 6900], [4100, 8350]]
RA-H04-U01 | RA | Room header | 04 | 129.954463 | 500 | 350 |  | 0.7426 | 0.02111 | 0.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3000, 7000], [3000, 6900]]
RA-H04-D01 | RA | Room header | 04 | 259.908926 | 500 | 350 |  | 1.48519 | 0.0726 | 2.6 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3000, 4300], [3000, 6900]]
RA-H04-D02 | RA | Room header | 04 | 129.954463 | 500 | 350 |  | 0.7426 | 0.02111 | 3.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[3000, 1000], [3000, 4300]]
RA-R04-01 | RA | Runout | 04 | 129.954463 | 300 |  | 300 | 1.83848 | 0.15755 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[700, 7000], [3000, 7000]]
RA-R04-02 | RA | Runout | 04 | 129.954463 | 300 |  | 300 | 1.83848 | 0.15755 | 1.9 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[4900, 4300], [3000, 4300]]
RA-R04-03 | RA | Runout | 04 | 129.954463 | 300 |  | 300 | 1.83848 | 0.15755 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[700, 1000], [3000, 1000]]
SA-B08 | SA | Branch | 08 | 884.6 | 600 | 400 |  | 3.68583 | 0.31325 | 4.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[7000, 9300], [7000, 6300], [8500, 6300]]
SA-H08-U01 | SA | Room header | 08 | 294.866667 | 600 | 400 |  | 1.22861 | 0.04276 | 0.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 6300], [8500, 6500]]
SA-H08-D01 | SA | Room header | 08 | 589.733333 | 600 | 400 |  | 2.45722 | 0.14933 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 6300], [8500, 4200]]
SA-H08-D02 | SA | Room header | 08 | 294.866667 | 600 | 400 |  | 1.22861 | 0.04276 | 2.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 4200], [8500, 1700]]
SA-R08-01 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 6500], [6500, 6500]]
SA-R08-02 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 6500], [10600, 6500]]
SA-R08-03 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 4200], [6500, 4200]]
SA-R08-04 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 4200], [10600, 4200]]
SA-R08-05 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 1700], [6500, 1700]]
SA-R08-06 | SA | Runout | 08 | 147.433333 | 325 |  | 325 | 1.77721 | 0.13426 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8500, 1700], [10600, 1700]]
RA-B08 | RA | Branch | 08 | 825.26339 | 700 | 450 |  | 2.61988 | 0.14282 | 2.85 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8900, 6900], [7500, 6900], [7500, 8350]]
RA-H08-U01 | RA | Room header | 08 | 275.087797 | 700 | 450 |  | 0.87329 | 0.01974 | 0.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8900, 7100], [8900, 6900]]
RA-H08-D01 | RA | Room header | 08 | 550.175593 | 700 | 450 |  | 1.74659 | 0.06843 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8900, 4600], [8900, 6900]]
RA-H08-D02 | RA | Room header | 08 | 275.087797 | 700 | 450 |  | 0.87329 | 0.01974 | 3.7 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[8900, 900], [8900, 4600]]
RA-R08-01 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 3.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[5900, 7100], [8900, 7100]]
RA-R08-02 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[11200, 7100], [8900, 7100]]
RA-R08-03 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 3.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[5900, 4600], [8900, 4600]]
RA-R08-04 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[11200, 4600], [8900, 4600]]
RA-R08-05 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 3.0 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[5900, 900], [8900, 900]]
RA-R08-06 | RA | Runout | 08 | 137.543898 | 300 |  | 300 | 1.94585 | 0.17449 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[11200, 900], [8900, 900]]
SA-B05 | SA | Branch | 05 | 777.7 | 600 | 350 |  | 3.70333 | 0.34926 | 12.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[1800, 13200], [14000, 13200]]
SA-H05-U01 | SA | Room header | 05 | 777.7 | 600 | 350 |  | 3.70333 | 0.34926 | 0.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 13200], [14000, 13600]]
SA-H05-U02 | SA | Room header | 05 | 466.62 | 600 | 350 |  | 2.222 | 0.13757 | 2.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 13600], [14000, 15800]]
SA-H05-U03 | SA | Room header | 05 | 311.08 | 600 | 350 |  | 1.48133 | 0.06619 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 15800], [14000, 18100]]
SA-R05-01 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 3.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 18100], [10900, 18100]]
SA-R05-02 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 2.6 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 18100], [16600, 18100]]
SA-R05-03 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 4.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 15800], [18300, 15800]]
SA-R05-04 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 3.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 13600], [10900, 13600]]
SA-R05-05 | SA | Runout | 05 | 155.54 | 325 |  | 325 | 1.87493 | 0.14783 | 2.6 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14000, 13600], [16600, 13600]]
RA-B05 | RA | Branch | 05 | 718.36339 | 650 | 400 |  | 2.76294 | 0.17796 | 11.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14900, 12200], [3500, 12200]]
RA-H05-U01 | RA | Room header | 05 | 574.690712 | 650 | 400 |  | 2.21035 | 0.11859 | 0.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14900, 12500], [14900, 12200]]
RA-H05-U02 | RA | Room header | 05 | 431.018034 | 650 | 400 |  | 1.65776 | 0.07049 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14900, 14600], [14900, 12500]]
RA-H05-U03 | RA | Room header | 05 | 287.345356 | 650 | 400 |  | 1.10517 | 0.03404 | 4.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14900, 18800], [14900, 14600]]
RA-H05-D01 | RA | Room header | 05 | 143.672678 | 650 | 400 |  | 0.55259 | 0.00995 | 1.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14900, 10700], [14900, 12200]]
RA-R05-01 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 5.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[9700, 18800], [14900, 18800]]
RA-R05-02 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 4.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[19000, 18800], [14900, 18800]]
RA-R05-03 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 5.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[9700, 14600], [14900, 14600]]
RA-R05-04 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 4.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[19000, 12500], [14900, 12500]]
RA-R05-05 | RA | Runout | 05 | 143.672678 | 300 |  | 300 | 2.03255 | 0.18875 | 0.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[15100, 10700], [14900, 10700]]
SA-B06 | SA | Branch | 06 | 418.2 | 450 | 300 |  | 3.09778 | 0.3238 | 2.1 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[11000, 9300], [11000, 10600], [11800, 10600]]
SA-H06-D01 | SA | Room header | 06 | 139.4 | 450 | 300 |  | 1.03259 | 0.04479 | 4.6 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[11800, 10600], [11800, 6000]]
SA-R06-01 | SA | Runout | 06 | 139.4 | 300 |  | 300 | 1.97211 | 0.17876 | 7.2 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[11800, 10600], [5400, 10600], [5400, 9800]]
SA-R06-02 | SA | Runout | 06 | 139.4 | 300 |  | 300 | 1.97211 | 0.17876 | 3.7 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[11800, 10600], [14700, 10600], [14700, 9800]]
SA-R06-03 | SA | Runout | 06 | 139.4 | 300 |  | 300 | 1.97211 | 0.17876 | 4.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[11800, 6000], [16300, 6000]]
RA-B06 | RA | Branch | 06 | 358.86339 | 550 | 350 |  | 1.86423 | 0.10428 | 6.05 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[13000, 10200], [13600, 10200], [13600, 7700], [11300, 7700], [11300, 8350]]
RA-H06-D01 | RA | Room header | 06 | 89.715847 | 550 | 350 |  | 0.46606 | 0.00886 | 4.6 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[13000, 5600], [13000, 10200]]
RA-R06-01 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 11.55 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[3100, 8550], [3100, 10200], [13000, 10200]]
RA-R06-02 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 4.95 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[9700, 8550], [9700, 10200], [13000, 10200]]
RA-R06-03 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 5.85 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[17200, 8550], [17200, 10200], [13000, 10200]]
RA-R06-04 | RA | Runout | 06 | 89.715847 | 300 |  | 300 | 1.26922 | 0.08116 | 2.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[15100, 5600], [13000, 5600]]
SA-B09 | SA | Branch | 09 | 46.2 | 200 | 150 |  | 1.54 | 0.23071 | 2.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[13200, 9300], [13200, 7100], [13000, 7100]]
SA-H09-D01 | SA | Room header | 09 | 46.2 | 200 | 150 |  | 1.54 | 0.23071 | 0.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[13000, 7100], [13000, 7000]]
SA-H09-D02 | SA | Room header | 09 | 23.1 | 200 | 150 |  | 0.77 | 0.06797 | 1.8 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[13000, 7000], [13000, 5200]]
SA-R09-01 | SA | Runout | 09 | 23.1 | 150 |  | 150 | 1.30719 | 0.20416 | 0.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[13000, 7000], [13200, 7000]]
SA-R09-02 | SA | Runout | 09 | 23.1 | 150 |  | 150 | 1.30719 | 0.20416 | 0.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[13000, 5200], [13200, 5200]]
SA-B07 | SA | Branch | 07 | 168.2 | 300 | 250 |  | 2.24267 | 0.2536 | 7.1 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[15500, 9300], [15500, 3600], [14100, 3600]]
SA-H07-D01 | SA | Room header | 07 | 168.2 | 300 | 250 |  | 2.24267 | 0.2536 | 0.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14100, 3600], [14100, 3200]]
SA-R07-01 | SA | Runout | 07 | 168.2 | 350 |  | 350 | 1.74824 | 0.11894 | 0.2 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14100, 3200], [13900, 3200]]
RA-B07 | RA | Branch | 07 | 108.86339 | 350 | 250 |  | 1.24415 | 0.08113 | 6.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[15000, 2200], [15350, 2200], [15350, 8350]]
RA-H07-D01 | RA | Room header | 07 | 108.86339 | 350 | 250 |  | 1.24415 | 0.08113 | 0.8 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[15000, 1400], [15000, 2200]]
RA-R07-01 | RA | Runout | 07 | 108.86339 | 300 |  | 300 | 1.5401 | 0.11467 | 0.6 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14400, 1400], [15000, 1400]]
SA-B03 | SA | Branch | 03 | 147.6 | 300 | 200 |  | 2.46 | 0.35111 | 2.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[17800, 9300], [17800, 7300], [18200, 7300]]
SA-H03-D01 | SA | Room header | 03 | 147.6 | 300 | 200 |  | 2.46 | 0.35111 | 0.7 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[18200, 7300], [18200, 6600]]
SA-R03-01 | SA | Runout | 03 | 147.6 | 325 |  | 325 | 1.77922 | 0.13453 | 0.4 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[18200, 6600], [18600, 6600]]
SA-B01 | SA | Branch | 01 | 141.3 | 300 | 200 |  | 2.355 | 0.32451 | 7.5 | TBC | BOD TBC | Rev07 proposed clearance route; avoids coincident mains / allows branch-device station. Levels and developed fitting length TBC | [[18500, 9300], [18500, 8800], [16800, 8800], [16800, 3500]]
SA-H01-D01 | SA | Room header | 01 | 141.3 | 300 | 200 |  | 2.355 | 0.32451 | 0.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[16800, 3500], [16800, 3200]]
SA-R01-01 | SA | Runout | 01 | 141.3 | 300 |  | 300 | 1.99899 | 0.18317 | 1.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[16800, 3200], [18100, 3200]]
EA-B09 | EA | Extract branch | 09 | 64.888889 | 250 | 200 |  | 1.29778 | 0.12286 | 6.7 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14700, 7000], [14700, 7600], [20800, 7600]]
EA-R09-01 | EA | Extract runout | 09 | 32.444444 | 150 |  | 150 | 1.83598 | 0.37327 | 0.5 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14200, 7000], [14700, 7000]]
EA-R09-02 | EA | Extract runout | 09 | 32.444444 | 150 |  | 150 | 1.83598 | 0.37327 | 2.3 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[14200, 5200], [14700, 5200], [14700, 7000]]
EA-B03 | EA | Extract branch | 03 | 147.6 | 300 | 200 |  | 2.46 | 0.35111 | 1.9 | TBC | BOD TBC | Proposed 2D centre-line; vertical length TBC | [[18900, 5700], [20800, 5700]]

## Transitions
tag | type | air | upstream | downstream | start_x_mm | start_y_mm | end_x_mm | end_y_mm | plan_mouth_mm | plan_neck_mm | proposed_length_mm | status
F-SA-RED-01 | Main tapered transition | SA | SA-M01 | SA-M02 | 1800.0 | 16207.5 | 1800.0 | 15857.5 | 1200.0 | 1100.0 | 350 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-SA-RED-02 | Main tapered transition | SA | SA-M02 | SA-M03 | 1800.0 | 12745.0 | 1800.0 | 12370.0 | 1100.0 | 950.0 | 375 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-SA-RED-03 | Main tapered transition | SA | SA-M03 | SA-M04 | 3861.2 | 9300.0 | 4211.2 | 9300.0 | 950.0 | 850.0 | 350 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-SA-RED-04 | Main tapered transition | SA | SA-M04 | SA-M05 | 7455.0 | 9300.0 | 7955.0 | 9300.0 | 850.0 | 650.0 | 500 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-SA-RED-05 | Main tapered transition | SA | SA-M05 | SA-M06 | 11361.2 | 9300.0 | 11736.2 | 9300.0 | 650.0 | 500.0 | 375 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-SA-RED-06 | Main tapered transition | SA | SA-M06 | SA-M07 | 13405.0 | 9300.0 | 13755.0 | 9300.0 | 500.0 | 450.0 | 350 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-SA-RED-07 | Main tapered transition | SA | SA-M07 | SA-M08 | 15767.5 | 9300.0 | 16117.5 | 9300.0 | 450.0 | 400.0 | 350 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-SA-RED-08 | Main tapered transition | SA | SA-M08 | SA-M09 | 18067.5 | 9300.0 | 18417.5 | 9300.0 | 400.0 | 300.0 | 350 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-RA-RED-01 | Main tapered transition | RA | RA-M02 | RA-M01 | 3500.0 | 16855.0 | 3500.0 | 17355.0 | 1400.0 | 1200.0 | 500 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-RA-RED-02 | Main tapered transition | RA | RA-M03 | RA-M02 | 3500.0 | 12686.2 | 3500.0 | 13561.2 | 1200.0 | 850.0 | 875 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-RA-RED-03 | Main tapered transition | RA | RA-M04 | RA-M03 | 4060.0 | 8350.0 | 3710.0 | 8350.0 | 850.0 | 800.0 | 350 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-RA-RED-04 | Main tapered transition | RA | RA-M05 | RA-M04 | 6982.5 | 8350.0 | 6607.5 | 8350.0 | 800.0 | 650.0 | 375 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
F-RA-RED-05 | Main tapered transition | RA | RA-M06 | RA-M05 | 10876.2 | 8350.0 | 10376.2 | 8350.0 | 650.0 | 450.0 | 500 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B02 | Tapered room-branch boot | SA | SA-M01 | SA-B02 | 2400.0 | 16600.0 | 2700.0 | 16600.0 | 625 | 500 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-B02 | Tapered room-branch boot | RA | RA-B02 | RA-M02 | 4100.0 | 16400.0 | 4400.0 | 16400.0 | 750 | 600 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B04 | Tapered room-branch boot | SA | SA-M03 | SA-B04 | 3500.0 | 8825.0 | 3500.0 | 8525.0 | 562 | 450 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-B04 | Tapered room-branch boot | RA | RA-B04 | RA-M04 | 4100.0 | 7950.0 | 4100.0 | 7650.0 | 625 | 500 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B08 | Tapered room-branch boot | SA | SA-M04 | SA-B08 | 7000.0 | 8875.0 | 7000.0 | 8575.0 | 750 | 600 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-B08 | Tapered room-branch boot | RA | RA-B08 | RA-M05 | 7500.0 | 8025.0 | 7500.0 | 7725.0 | 875 | 700 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B05 | Tapered room-branch boot | SA | SA-M02 | SA-B05 | 2350.0 | 13200.0 | 2650.0 | 13200.0 | 750 | 600 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-B05 | Tapered room-branch boot | RA | RA-B05 | RA-M03 | 3925.0 | 12200.0 | 4225.0 | 12200.0 | 812 | 650 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B06 | Tapered room-branch boot | SA | SA-M05 | SA-B06 | 11000.0 | 9625.0 | 11000.0 | 9925.0 | 562 | 450 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-B06 | Tapered room-branch boot | RA | RA-B06 | RA-M06 | 11300.0 | 8125.0 | 11300.0 | 7870.0 | 688 | 550 | 255 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B09 | Tapered room-branch boot | SA | SA-M06 | SA-B09 | 13200.0 | 9050.0 | 13200.0 | 8750.0 | 250 | 200 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B07 | Tapered room-branch boot | SA | SA-M07 | SA-B07 | 15500.0 | 9075.0 | 15500.0 | 8775.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-B07 | Tapered room-branch boot | RA | RA-B07 | RA-M06 | 15350.0 | 8125.0 | 15350.0 | 7825.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B03 | Tapered room-branch boot | SA | SA-M08 | SA-B03 | 17800.0 | 9100.0 | 17800.0 | 8800.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-B01 | Tapered room-branch boot | SA | SA-M09 | SA-B01 | 18500.0 | 9150.0 | 18500.0 | 8940.0 | 375 | 300 | 210 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R02-01 | Rectangular-to-round terminal adaptor | SA | SA-H02-U01 | SA-R02-01 | 4550.0 | 18000.0 | 4250.0 | 18000.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R02-02 | Rectangular-to-round terminal adaptor | SA | SA-H02-U01 | SA-R02-02 | 5050.0 | 18000.0 | 5350.0 | 18000.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R02-03 | Rectangular-to-round terminal adaptor | SA | SA-H02-D01 | SA-R02-03 | 4550.0 | 13100.0 | 4250.0 | 13100.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R02-04 | Rectangular-to-round terminal adaptor | SA | SA-H02-D01 | SA-R02-04 | 5050.0 | 13100.0 | 5350.0 | 13100.0 | 438 | 350 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R02-01 | Rectangular-to-round terminal adaptor | RA | RA-R02-01 | RA-H02-U01 | 5700.0 | 17000.0 | 5400.0 | 17000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R02-02 | Rectangular-to-round terminal adaptor | RA | RA-R02-02 | RA-H02-U01 | 6300.0 | 17000.0 | 6600.0 | 17000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R02-03 | Rectangular-to-round terminal adaptor | RA | RA-R02-03 | RA-H02-D01 | 5700.0 | 11900.0 | 5400.0 | 11900.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R02-04 | Rectangular-to-round terminal adaptor | RA | RA-R02-04 | RA-H02-D01 | 6300.0 | 11900.0 | 6600.0 | 11900.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R04-01 | Rectangular-to-round terminal adaptor | SA | SA-H04-U01 | SA-R04-01 | 2675.0 | 6600.0 | 2375.0 | 6600.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R04-02 | Rectangular-to-round terminal adaptor | SA | SA-H04-D01 | SA-R04-02 | 3125.0 | 4300.0 | 3425.0 | 4300.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R04-03 | Rectangular-to-round terminal adaptor | SA | SA-H04-D02 | SA-R04-03 | 2675.0 | 1900.0 | 2375.0 | 1900.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R04-01 | Rectangular-to-round terminal adaptor | RA | RA-R04-01 | RA-H04-U01 | 2750.0 | 7000.0 | 2450.0 | 7000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R04-02 | Rectangular-to-round terminal adaptor | RA | RA-R04-02 | RA-H04-D01 | 3250.0 | 4300.0 | 3550.0 | 4300.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R04-03 | Rectangular-to-round terminal adaptor | RA | RA-R04-03 | RA-H04-D02 | 2750.0 | 1000.0 | 2450.0 | 1000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-01 | Rectangular-to-round terminal adaptor | SA | SA-H08-U01 | SA-R08-01 | 8200.0 | 6500.0 | 7900.0 | 6500.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-02 | Rectangular-to-round terminal adaptor | SA | SA-H08-U01 | SA-R08-02 | 8800.0 | 6500.0 | 9100.0 | 6500.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-03 | Rectangular-to-round terminal adaptor | SA | SA-H08-D01 | SA-R08-03 | 8200.0 | 4200.0 | 7900.0 | 4200.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-04 | Rectangular-to-round terminal adaptor | SA | SA-H08-D01 | SA-R08-04 | 8800.0 | 4200.0 | 9100.0 | 4200.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-05 | Rectangular-to-round terminal adaptor | SA | SA-H08-D02 | SA-R08-05 | 8200.0 | 1700.0 | 7900.0 | 1700.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R08-06 | Rectangular-to-round terminal adaptor | SA | SA-H08-D02 | SA-R08-06 | 8800.0 | 1700.0 | 9100.0 | 1700.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R08-01 | Rectangular-to-round terminal adaptor | RA | RA-R08-01 | RA-H08-U01 | 8550.0 | 7100.0 | 8250.0 | 7100.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R08-02 | Rectangular-to-round terminal adaptor | RA | RA-R08-02 | RA-H08-U01 | 9250.0 | 7100.0 | 9550.0 | 7100.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R08-03 | Rectangular-to-round terminal adaptor | RA | RA-R08-03 | RA-H08-D01 | 8550.0 | 4600.0 | 8250.0 | 4600.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R08-04 | Rectangular-to-round terminal adaptor | RA | RA-R08-04 | RA-H08-D01 | 9250.0 | 4600.0 | 9550.0 | 4600.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R08-05 | Rectangular-to-round terminal adaptor | RA | RA-R08-05 | RA-H08-D02 | 8550.0 | 900.0 | 8250.0 | 900.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R08-06 | Rectangular-to-round terminal adaptor | RA | RA-R08-06 | RA-H08-D02 | 9250.0 | 900.0 | 9550.0 | 900.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-01 | Rectangular-to-round terminal adaptor | SA | SA-H05-U03 | SA-R05-01 | 13700.0 | 18100.0 | 13400.0 | 18100.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-02 | Rectangular-to-round terminal adaptor | SA | SA-H05-U03 | SA-R05-02 | 14300.0 | 18100.0 | 14600.0 | 18100.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-03 | Rectangular-to-round terminal adaptor | SA | SA-H05-U02 | SA-R05-03 | 14300.0 | 15800.0 | 14600.0 | 15800.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-04 | Rectangular-to-round terminal adaptor | SA | SA-H05-U01 | SA-R05-04 | 13700.0 | 13600.0 | 13400.0 | 13600.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R05-05 | Rectangular-to-round terminal adaptor | SA | SA-H05-U01 | SA-R05-05 | 14300.0 | 13600.0 | 14600.0 | 13600.0 | 406 | 325 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R05-01 | Rectangular-to-round terminal adaptor | RA | RA-R05-01 | RA-H05-U03 | 14575.0 | 18800.0 | 14275.0 | 18800.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R05-02 | Rectangular-to-round terminal adaptor | RA | RA-R05-02 | RA-H05-U03 | 15225.0 | 18800.0 | 15525.0 | 18800.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R05-03 | Rectangular-to-round terminal adaptor | RA | RA-R05-03 | RA-H05-U02 | 14575.0 | 14600.0 | 14275.0 | 14600.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R05-04 | Rectangular-to-round terminal adaptor | RA | RA-R05-04 | RA-H05-U01 | 15225.0 | 12500.0 | 15525.0 | 12500.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R06-01 | Rectangular-to-round terminal adaptor | SA | SA-B06 | SA-R06-01 | 11800.0 | 10600.0 | 11500.0 | 10600.0 | 450 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R06-02 | Rectangular-to-round terminal adaptor | SA | SA-B06 | SA-R06-02 | 11800.0 | 10600.0 | 12100.0 | 10600.0 | 450 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R06-03 | Rectangular-to-round terminal adaptor | SA | SA-H06-D01 | SA-R06-03 | 12025.0 | 6000.0 | 12325.0 | 6000.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R06-01 | Rectangular-to-round terminal adaptor | RA | RA-R06-01 | RA-B06 | 13000.0 | 10200.0 | 12700.0 | 10200.0 | 550 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R06-02 | Rectangular-to-round terminal adaptor | RA | RA-R06-02 | RA-B06 | 13000.0 | 10200.0 | 12700.0 | 10200.0 | 550 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R06-03 | Rectangular-to-round terminal adaptor | RA | RA-R06-03 | RA-B06 | 13000.0 | 10200.0 | 13300.0 | 10200.0 | 550 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R06-04 | Rectangular-to-round terminal adaptor | RA | RA-R06-04 | RA-H06-D01 | 13275.0 | 5600.0 | 13575.0 | 5600.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R09-01 | Rectangular-to-round terminal adaptor | SA | SA-H09-D01 | SA-R09-01 | 13100.0 | 7000.0 | 13200.0 | 7000.0 | 188 | 150 | 100 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R09-02 | Rectangular-to-round terminal adaptor | SA | SA-H09-D02 | SA-R09-02 | 13100.0 | 5200.0 | 13200.0 | 5200.0 | 188 | 150 | 100 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-RA-R07-01 | Rectangular-to-round terminal adaptor | RA | RA-R07-01 | RA-H07-D01 | 14825.0 | 1400.0 | 14570.0 | 1400.0 | 375 | 300 | 255 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R03-01 | Rectangular-to-round terminal adaptor | SA | SA-H03-D01 | SA-R03-01 | 18350.0 | 6600.0 | 18500.0 | 6600.0 | 406 | 325 | 150 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-SA-R01-01 | Rectangular-to-round terminal adaptor | SA | SA-H01-D01 | SA-R01-01 | 16950.0 | 3200.0 | 17250.0 | 3200.0 | 375 | 300 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-EA-R09-01 | Rectangular-to-round terminal adaptor | EA | EA-R09-01 | EA-B09 | 14575.0 | 7000.0 | 14350.0 | 7000.0 | 188 | 150 | 225 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC
TR-EA-R09-02 | Rectangular-to-round terminal adaptor | EA | EA-R09-02 | EA-B09 | 14700.0 | 7000.0 | 14700.0 | 6700.0 | 250 | 150 | 300 | Proposed plan geometry; height conversion / fitting K / fabrication development TBC

## Fittings
tag | section | type | x_mm | y_mm | loss_K | basis
F-SA-M03-B01 | SA-M03 | 90 deg miter bend / turning vanes | 1800 | 9300 | TBC selected fitting | Proposed geometry
F-RA-M03-B01 | RA-M03 | 90 deg miter bend / turning vanes | 3500 | 8350 | TBC selected fitting | Proposed geometry
F-SA-RED-01 | SA-M01 | Transition / reducer | 1800.0 | 16032.5 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 350 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-RED-02 | SA-M02 | Transition / reducer | 1800.0 | 12557.5 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 375 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-RED-03 | SA-M03 | Transition / reducer | 4036.2 | 9300.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 350 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-RED-04 | SA-M04 | Transition / reducer | 7705.0 | 9300.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 500 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-RED-05 | SA-M05 | Transition / reducer | 11548.8 | 9300.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 375 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-RED-06 | SA-M06 | Transition / reducer | 13580.0 | 9300.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 350 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-RED-07 | SA-M07 | Transition / reducer | 15942.5 | 9300.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 350 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-RED-08 | SA-M08 | Transition / reducer | 18242.5 | 9300.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 350 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-RA-RED-01 | RA-M01 | Transition / reducer | 3500.0 | 17105.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 500 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-RA-RED-02 | RA-M02 | Transition / reducer | 3500.0 | 13123.8 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 875 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-RA-RED-03 | RA-M03 | Transition / reducer | 3885.0 | 8350.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 350 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-RA-RED-04 | RA-M04 | Transition / reducer | 6795.0 | 8350.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 375 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-RA-RED-05 | RA-M05 | Transition / reducer | 10626.2 | 8350.0 | TBC geometry / ASHRAE fitting | Rev08 continuous taper; proposed axial length 500 mm; section W x H per schedule. Selected fitting K and fabrication development TBC
F-SA-TEE-02 | SA-B02 | Main-to-room take-off / tee | 1800 | 16600 | TBC actual fitting | Proposed
F-SA-HDR-02-01 | SA-B02 | Header-to-terminal take-off | 4800 | 18000 | TBC selected fitting | Proposed
F-SA-HDR-02-02 | SA-B02 | Header-to-terminal take-off | 4800 | 18000 | TBC selected fitting | Proposed
F-SA-HDR-02-03 | SA-B02 | Header-to-terminal take-off | 4800 | 13100 | TBC selected fitting | Proposed
F-SA-HDR-02-04 | SA-B02 | Header-to-terminal take-off | 4800 | 13100 | TBC selected fitting | Proposed
F-RA-TEE-02 | RA-B02 | Room-to-main junction | 3500 | 16400 | TBC actual fitting | Proposed
F-RA-HDR-02-01 | RA-B02 | Header-to-terminal take-off | 4400 | 16800 | TBC selected fitting | Proposed
F-RA-HDR-02-02 | RA-B02 | Header-to-terminal take-off | 4400 | 16800 | TBC selected fitting | Proposed
F-RA-HDR-02-03 | RA-B02 | Header-to-terminal take-off | 4400 | 11900 | TBC selected fitting | Proposed
F-RA-HDR-02-04 | RA-B02 | Header-to-terminal take-off | 4400 | 11900 | TBC selected fitting | Proposed
F-SA-B04-B01 | SA-B04 | 90 deg miter bend / turning vanes | 3500 | 6500 | TBC selected fitting | Proposed geometry
F-SA-TEE-04 | SA-B04 | Main-to-room take-off / tee | 3500 | 9300 | TBC actual fitting | Proposed
F-SA-HDR-04-01 | SA-B04 | Header-to-terminal take-off | 2900 | 6600 | TBC selected fitting | Proposed
F-SA-HDR-04-02 | SA-B04 | Header-to-terminal take-off | 2900 | 4300 | TBC selected fitting | Proposed
F-SA-HDR-04-03 | SA-B04 | Header-to-terminal take-off | 2900 | 1900 | TBC selected fitting | Proposed
F-RA-B04-B01 | RA-B04 | 90 deg miter bend / turning vanes | 4100 | 6900 | TBC selected fitting | Proposed geometry
F-RA-TEE-04 | RA-B04 | Room-to-main junction | 4100 | 8350 | TBC actual fitting | Proposed
F-RA-HDR-04-01 | RA-B04 | Header-to-terminal take-off | 3000 | 7000 | TBC selected fitting | Proposed
F-RA-HDR-04-02 | RA-B04 | Header-to-terminal take-off | 3000 | 4300 | TBC selected fitting | Proposed
F-RA-HDR-04-03 | RA-B04 | Header-to-terminal take-off | 3000 | 1000 | TBC selected fitting | Proposed
F-SA-B08-B01 | SA-B08 | 90 deg miter bend / turning vanes | 7000 | 6300 | TBC selected fitting | Proposed geometry
F-SA-TEE-08 | SA-B08 | Main-to-room take-off / tee | 7000 | 9300 | TBC actual fitting | Proposed
F-SA-HDR-08-01 | SA-B08 | Header-to-terminal take-off | 8500 | 6500 | TBC selected fitting | Proposed
F-SA-HDR-08-02 | SA-B08 | Header-to-terminal take-off | 8500 | 6500 | TBC selected fitting | Proposed
F-SA-HDR-08-03 | SA-B08 | Header-to-terminal take-off | 8500 | 4200 | TBC selected fitting | Proposed
F-SA-HDR-08-04 | SA-B08 | Header-to-terminal take-off | 8500 | 4200 | TBC selected fitting | Proposed
F-SA-HDR-08-05 | SA-B08 | Header-to-terminal take-off | 8500 | 1700 | TBC selected fitting | Proposed
F-SA-HDR-08-06 | SA-B08 | Header-to-terminal take-off | 8500 | 1700 | TBC selected fitting | Proposed
F-RA-B08-B01 | RA-B08 | 90 deg miter bend / turning vanes | 7500 | 6900 | TBC selected fitting | Proposed geometry
F-RA-TEE-08 | RA-B08 | Room-to-main junction | 7500 | 8350 | TBC actual fitting | Proposed
F-RA-HDR-08-01 | RA-B08 | Header-to-terminal take-off | 8900 | 7100 | TBC selected fitting | Proposed
F-RA-HDR-08-02 | RA-B08 | Header-to-terminal take-off | 8900 | 7100 | TBC selected fitting | Proposed
F-RA-HDR-08-03 | RA-B08 | Header-to-terminal take-off | 8900 | 4600 | TBC selected fitting | Proposed
F-RA-HDR-08-04 | RA-B08 | Header-to-terminal take-off | 8900 | 4600 | TBC selected fitting | Proposed
F-RA-HDR-08-05 | RA-B08 | Header-to-terminal take-off | 8900 | 900 | TBC selected fitting | Proposed
F-RA-HDR-08-06 | RA-B08 | Header-to-terminal take-off | 8900 | 900 | TBC selected fitting | Proposed
F-SA-TEE-05 | SA-B05 | Main-to-room take-off / tee | 1800 | 13200 | TBC actual fitting | Proposed
F-SA-HDR-05-01 | SA-B05 | Header-to-terminal take-off | 14000 | 18100 | TBC selected fitting | Proposed
F-SA-HDR-05-02 | SA-B05 | Header-to-terminal take-off | 14000 | 18100 | TBC selected fitting | Proposed
F-SA-HDR-05-03 | SA-B05 | Header-to-terminal take-off | 14000 | 15800 | TBC selected fitting | Proposed
F-SA-HDR-05-04 | SA-B05 | Header-to-terminal take-off | 14000 | 13600 | TBC selected fitting | Proposed
F-SA-HDR-05-05 | SA-B05 | Header-to-terminal take-off | 14000 | 13600 | TBC selected fitting | Proposed
F-RA-TEE-05 | RA-B05 | Room-to-main junction | 3500 | 12200 | TBC actual fitting | Proposed
F-RA-HDR-05-01 | RA-B05 | Header-to-terminal take-off | 14900 | 18800 | TBC selected fitting | Proposed
F-RA-HDR-05-02 | RA-B05 | Header-to-terminal take-off | 14900 | 18800 | TBC selected fitting | Proposed
F-RA-HDR-05-03 | RA-B05 | Header-to-terminal take-off | 14900 | 14600 | TBC selected fitting | Proposed
F-RA-HDR-05-04 | RA-B05 | Header-to-terminal take-off | 14900 | 12500 | TBC selected fitting | Proposed
F-RA-HDR-05-05 | RA-B05 | Header-to-terminal take-off | 14900 | 10700 | TBC selected fitting | Proposed
F-SA-TEE-06 | SA-B06 | Main-to-room take-off / tee | 11000 | 9300 | TBC actual fitting | Proposed
F-SA-HDR-06-01 | SA-B06 | Header-to-terminal take-off | 11800 | 9800 | TBC selected fitting | Proposed
F-SA-HDR-06-02 | SA-B06 | Header-to-terminal take-off | 11800 | 9800 | TBC selected fitting | Proposed
F-SA-HDR-06-03 | SA-B06 | Header-to-terminal take-off | 11800 | 6000 | TBC selected fitting | Proposed
F-RA-TEE-06 | RA-B06 | Room-to-main junction | 11300 | 8350 | TBC actual fitting | Proposed
F-RA-HDR-06-01 | RA-B06 | Header-to-terminal take-off | 13000 | 8550 | TBC selected fitting | Proposed
F-RA-HDR-06-02 | RA-B06 | Header-to-terminal take-off | 13000 | 8550 | TBC selected fitting | Proposed
F-RA-HDR-06-03 | RA-B06 | Header-to-terminal take-off | 13000 | 8550 | TBC selected fitting | Proposed
F-RA-HDR-06-04 | RA-B06 | Header-to-terminal take-off | 13000 | 5600 | TBC selected fitting | Proposed
F-SA-B09-B01 | SA-B09 | 90 deg miter bend / turning vanes | 13200 | 7100 | TBC selected fitting | Proposed geometry
F-SA-TEE-09 | SA-B09 | Main-to-room take-off / tee | 13200 | 9300 | TBC actual fitting | Proposed
F-SA-HDR-09-01 | SA-B09 | Header-to-terminal take-off | 13000 | 7000 | TBC selected fitting | Proposed
F-SA-HDR-09-02 | SA-B09 | Header-to-terminal take-off | 13000 | 5200 | TBC selected fitting | Proposed
F-SA-B07-B01 | SA-B07 | 90 deg miter bend / turning vanes | 15500 | 3600 | TBC selected fitting | Proposed geometry
F-SA-TEE-07 | SA-B07 | Main-to-room take-off / tee | 15500 | 9300 | TBC actual fitting | Proposed
F-SA-HDR-07-01 | SA-B07 | Header-to-terminal take-off | 14100 | 3200 | TBC selected fitting | Proposed
F-RA-B07-B01 | RA-B07 | 90 deg miter bend / turning vanes | 15350 | 2200 | TBC selected fitting | Proposed geometry
F-RA-TEE-07 | RA-B07 | Room-to-main junction | 15350 | 8350 | TBC actual fitting | Proposed
F-RA-HDR-07-01 | RA-B07 | Header-to-terminal take-off | 15000 | 1400 | TBC selected fitting | Proposed
F-SA-B03-B01 | SA-B03 | 90 deg miter bend / turning vanes | 17800 | 7300 | TBC selected fitting | Proposed geometry
F-SA-TEE-03 | SA-B03 | Main-to-room take-off / tee | 17800 | 9300 | TBC actual fitting | Proposed
F-SA-HDR-03-01 | SA-B03 | Header-to-terminal take-off | 18200 | 6600 | TBC selected fitting | Proposed
F-SA-TEE-01 | SA-B01 | Main-to-room take-off / tee | 18500 | 9300 | TBC actual fitting | Proposed
F-SA-HDR-01-01 | SA-B01 | Header-to-terminal take-off | 16800 | 3200 | TBC selected fitting | Proposed
F-EA-B09-B01 | EA-B09 | 90 deg miter bend / turning vanes | 14700 | 7600 | TBC selected fitting | Proposed geometry
F-EA-R09-02-B01 | EA-R09-02 | 90 deg miter bend / turning vanes | 14700 | 5200 | TBC selected fitting | Proposed geometry
F-SA-B01-B01 | SA-B01 | 90 deg bend / turning vanes | 18500 | 8800 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-SA-B01-B02 | SA-B01 | 90 deg bend / turning vanes | 16800 | 8800 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-SA-B06-B01 | SA-B06 | 90 deg bend / turning vanes | 11000 | 10600 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-RA-B06-B01 | RA-B06 | 90 deg bend / turning vanes | 13600 | 10200 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-RA-B06-B02 | RA-B06 | 90 deg bend / turning vanes | 13600 | 7700 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-RA-B06-B03 | RA-B06 | 90 deg bend / turning vanes | 11300 | 7700 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-SA-R06-01-B01 | SA-R06-01 | 90 deg bend / turning vanes | 5400 | 10600 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-SA-R06-02-B01 | SA-R06-02 | 90 deg bend / turning vanes | 14700 | 10600 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-RA-R06-01-B01 | RA-R06-01 | 90 deg bend / turning vanes | 3100 | 10200 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-RA-R06-02-B01 | RA-R06-02 | 90 deg bend / turning vanes | 9700 | 10200 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC
F-RA-R06-03-B01 | RA-R06-03 | 90 deg bend / turning vanes | 17200 | 10200 | TBC selected fitting | Rev08 proposed clearance route; actual elbow development / elevation TBC

## Terminals
tag | room | air_type | flow_l_s | neck_dia_mm | face_w_mm | face_h_mm | x_mm | y_mm | level | catalogue
SD-02-01 | 02 | SA | 166.2 | 350 | 600 | 600 | 2700 | 18000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-02 | 02 | SA | 166.2 | 350 | 600 | 600 | 7100 | 18000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-03 | 02 | SA | 166.2 | 350 | 600 | 600 | 2700 | 13100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-02-04 | 02 | SA | 166.2 | 350 | 600 | 600 | 7100 | 13100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-02-01 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 1200 | 17000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-02 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 7700 | 17000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-03 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 1200 | 11900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-02-04 | 02 | RA | 151.36584740090174 | 300 | 500 | 500 | 7700 | 11900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-04-01 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 1800 | 6600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-04-02 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 4300 | 4300 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-04-03 | 04 | SA | 149.73333333333332 | 325 | 600 | 600 | 1900 | 1900 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-04-01 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 700 | 7000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-04-02 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 4900 | 4300 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-04-03 | 04 | RA | 129.95446320120234 | 300 | 500 | 500 | 700 | 1000 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-08-01 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6500 | 6500 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-02 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 6500 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-03 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6500 | 4200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-04 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 4200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-05 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 6500 | 1700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-08-06 | 08 | SA | 147.43333333333334 | 325 | 600 | 600 | 10600 | 1700 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-08-01 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5900 | 7100 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-02 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11200 | 7100 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-03 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5900 | 4600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-04 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11200 | 4600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-05 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 5900 | 900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-08-06 | 08 | RA | 137.54389826726785 | 300 | 500 | 500 | 11200 | 900 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-05-01 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 10900 | 18100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-02 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 16600 | 18100 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-03 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 18300 | 15800 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-04 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 10900 | 13600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-05-05 | 05 | SA | 155.54000000000002 | 325 | 600 | 600 | 16600 | 13600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-05-01 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 9700 | 18800 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-02 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 19000 | 18800 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-03 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 9700 | 14600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-04 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 19000 | 12500 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-05-05 | 05 | RA | 143.6726779207214 | 300 | 500 | 500 | 15100 | 10700 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-06-01 | 06 | SA | 139.4 | 300 | 600 | 600 | 5400 | 9800 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-06-02 | 06 | SA | 139.4 | 300 | 600 | 600 | 14700 | 9800 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-06-03 | 06 | SA | 139.4 | 300 | 600 | 600 | 16300 | 6000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-06-01 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 3100 | 8550 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-02 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 9700 | 8550 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-03 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 17200 | 8550 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
RG-06-04 | 06 | RA | 89.71584740090175 | 300 | 500 | 500 | 15100 | 5600 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-09-01 | 09 | SA | 23.1 | 150 | 300 | 300 | 13200 | 7000 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-09-02 | 09 | SA | 23.1 | 150 | 300 | 300 | 13200 | 5200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-07-01 | 07 | SA | 168.2 | 350 | 600 | 600 | 13900 | 3200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
RG-07-01 | 07 | RA | 108.863389603607 | 300 | 500 | 500 | 14400 | 1400 | Ceiling / BOD TBC | TBC; 60% free area is teaching assumption only
SD-03-01 | 03 | SA | 147.6 | 325 | 600 | 600 | 18600 | 6600 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
SD-01-01 | 01 | SA | 141.3 | 300 | 600 | 600 | 18100 | 3200 | Ceiling / BOD TBC | TBC; neck chosen for <=2 m/s, model / throw / NC / loss unverified
EG-09-01 | 09 | EA | 32.44444444444444 | 150 | 300 | 300 | 14200 | 7000 | Pickup height TBC | TBC
EG-09-02 | 09 | EA | 32.44444444444444 | 150 | 300 | 300 | 14200 | 5200 | Pickup height TBC | TBC
EG-03-01 | 03 | EA | 147.6 | 300 | 500 | 500 | 18900 | 5700 | Pickup height TBC | TBC
EG-01-01 | 01 | EA | TBC | TBC | 500 | 500 | 18600 | 1500 | Pickup height TBC | TBC

## Components
tag | service | basis | selection_status
VCD-S02 | Supply branch balancing damper | Room GF-02 | Proposed; OEM selection TBC
FSD-S02 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-02-01 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-02 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-03 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
SD-02-04 | Supply diffuser with integral OBD | Room GF-02; 166.200 L/s | Proposed; OEM selection TBC
RCD-R02 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R02 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-02-01 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-02 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-03 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
RG-02-04 | Ducted return grille with OBD | Room GF-02; 151.366 L/s | Proposed; OEM selection TBC
VCD-S04 | Supply branch balancing damper | Room GF-04 | Proposed; OEM selection TBC
FSD-S04 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-04-01 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
SD-04-02 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
SD-04-03 | Supply diffuser with integral OBD | Room GF-04; 149.733 L/s | Proposed; OEM selection TBC
RCD-R04 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R04 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-04-01 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
RG-04-02 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
RG-04-03 | Ducted return grille with OBD | Room GF-04; 129.954 L/s | Proposed; OEM selection TBC
EH-04 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S08 | Supply branch balancing damper | Room GF-08 | Proposed; OEM selection TBC
FSD-S08 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-08-01 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-02 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-03 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-04 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-05 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
SD-08-06 | Supply diffuser with integral OBD | Room GF-08; 147.433 L/s | Proposed; OEM selection TBC
RCD-R08 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R08 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-08-01 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-02 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-03 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-04 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-05 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
RG-08-06 | Ducted return grille with OBD | Room GF-08; 137.544 L/s | Proposed; OEM selection TBC
VCD-S05 | Supply branch balancing damper | Room GF-05 | Proposed; OEM selection TBC
FSD-S05 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-05-01 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-02 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-03 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-04 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
SD-05-05 | Supply diffuser with integral OBD | Room GF-05; 155.540 L/s | Proposed; OEM selection TBC
RCD-R05 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R05 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-05-01 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-02 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-03 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-04 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
RG-05-05 | Ducted return grille with OBD | Room GF-05; 143.673 L/s | Proposed; OEM selection TBC
EH-05 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S06 | Supply branch balancing damper | Room GF-06 | Proposed; OEM selection TBC
FSD-S06 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-06-01 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
SD-06-02 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
SD-06-03 | Supply diffuser with integral OBD | Room GF-06; 139.400 L/s | Proposed; OEM selection TBC
RCD-R06 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R06 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-06-01 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-02 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-03 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
RG-06-04 | Ducted return grille with OBD | Room GF-06; 89.716 L/s | Proposed; OEM selection TBC
EH-06 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S09 | Supply branch balancing damper | Room GF-09 | Proposed; OEM selection TBC
FSD-S09 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-09-01 | Supply diffuser with integral OBD | Room GF-09; 23.100 L/s | Proposed; OEM selection TBC
SD-09-02 | Supply diffuser with integral OBD | Room GF-09; 23.100 L/s | Proposed; OEM selection TBC
VCD-S07 | Supply branch balancing damper | Room GF-07 | Proposed; OEM selection TBC
FSD-S07 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-07-01 | Supply diffuser with integral OBD | Room GF-07; 168.200 L/s | Proposed; OEM selection TBC
RCD-R07 | Modulating room return damper | Proposed +50 Pa pressure control; provisional fixed-return starting balance | Proposed; OEM selection TBC
FSD-R07 | Conditional fire/smoke damper | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
RG-07-01 | Ducted return grille with OBD | Room GF-07; 108.863 L/s | Proposed; OEM selection TBC
EH-07 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S03 | Supply branch balancing damper | Room GF-03 | Proposed; OEM selection TBC
FSD-S03 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-03-01 | Supply diffuser with integral OBD | Room GF-03; 147.600 L/s | Proposed; OEM selection TBC
EH-03 | Indoor room comfort duct heater | 7.8.2; load / losses / high-limit and airflow proof TBC | Proposed; OEM selection TBC
VCD-S01 | Supply branch balancing damper | Room GF-01 | Proposed; OEM selection TBC
FSD-S01 | Conditional fire/smoke damper at rated penetration | Compartment / cause-and-effect approval required | Conditional; quantity and rating TBC
SD-01-01 | Supply diffuser with integral OBD | Room GF-01; 141.300 L/s | Proposed; OEM selection TBC
EG-09-01 | Dedicated extract grille | GF-09; final pickup height / model TBC | Proposed; OEM selection TBC
EG-09-02 | Dedicated extract grille | GF-09; final pickup height / model TBC | Proposed; OEM selection TBC
MD-IE09-01 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-09-01 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E09-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
MD-IE09-02 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-09-02 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E09-02 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
EG-03-01 | Dedicated extract grille | GF-03; final pickup height / model TBC | Proposed; OEM selection TBC
MD-IE03-01 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-03-01 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E03-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
MD-IE03-02 | Motorized extract fan inlet isolation | 7.14.1 isolation provision; final individual outlet arrangement to confirm | Proposed; OEM selection TBC
EF-03-02 | Axial extract fan | 7.19.1 2 x 100% | Proposed; OEM selection TBC
MD-E03-02 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
EG-01-01 | Dedicated extract grille | GF-01; final pickup height / model TBC | Proposed; OEM selection TBC
EF-01-01 | Clean-agent extract fan | One fan shown; quantity / agent suitability TBC | Proposed; OEM selection TBC
MD-E01-01 | Motorized fan isolation damper | 7.14.1; standby discharge isolation | Proposed; OEM selection TBC
HPCP-01 | Dedicated PLC HVAC power and control panel | 15.1 / 15.10 / 15.11; 20% spare I/O and CPU; separate duty / standby modules | Proposed; OEM selection TBC
HMI-01 | Local colour touchscreen HMI, >=10 inch | 15.12.1; alarms, trends, security, operating hours and energy | Proposed; OEM selection TBC
BMS-IF-01 | BMS / SCADA interface and operator workstation | 8.5.1 / 8.5.2; protocol and point mapping TBC | Proposed; OEM selection TBC
STL-01 | Outdoor sand trap louver / bird mesh | 7.12.1 / 7.7.1; mesh <=13 mm; SS316L when within 5 km of sea | Proposed; OEM selection TBC
F-OA-01 | Washable MERV 8 outdoor intake filter | 7.12.1; clean / dirty loss and face area TBC | Proposed; OEM selection TBC
OA-SIL-01 | Common outdoor intake sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
EA-SIL-03 | Dedicated extract sound attenuator | GF-03; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
EA-SIL-09 | Dedicated extract sound attenuator | GF-09; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
EA-SIL-01 | Dedicated extract sound attenuator | GF-01; catalogue loss / insertion loss TBC | Proposed; OEM selection TBC
STL-B1 | Cable basement sand trap louver / bird mesh | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
F-OA-B1 | Basement intake MERV 8 filter | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
OA-SIL-B1 | Basement intake sound attenuator | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
EA-SIL-B1-01 | Basement extract sound attenuator 1 | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
EA-SIL-B1-02 | Basement extract sound attenuator 2 | Proposed ventilation inlet / outlet arrangement; catalogue loss and final area TBC | Proposed; OEM selection TBC
MD-OA-01 | Common outdoor-air modulating damper | Proposed minimum OA / building pressure control; final OA TBC | Proposed; OEM selection TBC
PRD-01 | Common outdoor relief path and relief control | 7.13 / user relief basis; Qrelief = QOA - 691.12 only under current assumed RA | Proposed; OEM selection TBC
SA-SIL-01 | Common supply sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
RA-SIL-01 | Common return sound attenuator | Catalogue insertion loss / pressure loss TBC | Proposed; OEM selection TBC
EH-COM-01 | Common indoor electric duct heater | 7.8.2; heating load / high-limit / airflow proof TBC | Proposed; OEM selection TBC
HUM-01 | Steam humidifier in main supply, if required | 7.10.1; conditional requirement / duty TBC | Conditional; humidity duty to verify
PAU-A | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-A | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-A | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-A | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-A | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-A | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-A | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
PAU-B | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-B | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-B | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-B | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-B | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-B | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-B | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
PAU-C | Packaged DX unit, 3 x 50% bank | 7.17.1; 1848.9 L/s per unit, 2 duty + 1 available; rotating duty pair | Proposed; OEM selection TBC
MD-RA-C | Unit return shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-OA-C | Unit outdoor-air shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
MD-SA-C | Unit supply shut-off damper | 7.14.1; close standby paths, open / close proof | Proposed; OEM selection TBC
F1-C | MERV 8 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
F2-C | MERV 14 filter bank | 9.3.2; washable prefilter / disposable bag final | Proposed; OEM selection TBC
CD-PAU-C | Coil drain pan, trapped drain and cleanout | OEM pressure-based trap geometry; pipe route / invert TBC | Proposed; OEM selection TBC
SF-B1-01 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-SF-B1-01 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-ISF-B1-01 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
SF-B1-02 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-SF-B1-02 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-ISF-B1-02 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
EF-B1-01 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-EF-B1-01 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-IEF-B1-01 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
EF-B1-02 | Cable basement axial ventilation fan | 7.18.3; each group 2 x 100%, final flow = greater of 4 ACH and heat duty | Proposed; OEM selection TBC
MD-EF-B1-02 | Basement fan motorized isolation | 7.14.1; standby isolated | Proposed; OEM selection TBC
MD-IEF-B1-02 | Basement fan motorized inlet isolation | 7.14.1; isolate both sides of parallel fan paths | Proposed; OEM selection TBC
AD-S02 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 02 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S08 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 08 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S09 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 09 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S03 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 03 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-S01 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 01 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R02 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 02 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R08 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 08 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-R07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H04 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 04 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H05 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 05 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H06 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 06 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H07 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 07 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-H03 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater 03 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC
AD-HCOM-01 | Duct access door for inspection / maintenance | Rev07 reference drafting convention; adjacent branch damper / heater COM-01 | Proposed location; access side / clear opening / ceiling hatch / OEM clearance TBC

## Device_locations
tag | service | room | x_mm | y_mm | rotation_deg | status
VCD-S02 | SA | 02 | 2800.0 | 16600.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S02 | SA | 02 | 3120.0 | 16350.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S02 | SA | 02 | 3750.0 | 16600.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
RCD-R02 | RA | 02 | 5600.0 | 16400.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-R02 | RA | 02 | 5300.0 | 16100.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-R02 | RA | 02 | 4900.0 | 16400.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S05 | SA | 05 | 4606.0 | 13200.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S05 | SA | 05 | 7168.0 | 12900.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S05 | SA | 05 | 9730.0 | 13200.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
EH-05 | SA | 05 | 12292.0 | 13200.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-H05 | SA | 05 | 12022.0 | 12900.0 | -0.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
RCD-R05 | RA | 05 | 10910.0 | 12200.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-R05 | RA | 05 | 8972.0 | 11875.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-R05 | RA | 05 | 6920.0 | 12200.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S04 | SA | 04 | 3500.0 | 8350.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S04 | SA | 04 | 3275.0 | 7900.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S04 | SA | 04 | 3500.0 | 7550.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
EH-04 | SA | 04 | 3500.0 | 7088.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-H04 | SA | 04 | 3275.0 | 7358.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
RCD-R04 | RA | 04 | 4100.0 | 7360.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-R04 | RA | 04 | 4350.0 | 7450.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-R04 | RA | 04 | 4100.0 | 7540.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S08 | SA | 08 | 7000.0 | 8300.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S08 | SA | 08 | 6700.0 | 7980.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S08 | SA | 08 | 7000.0 | 7350.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
RCD-R08 | RA | 08 | 7500.0 | 7190.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-R08 | RA | 08 | 7850.0 | 7340.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-R08 | RA | 08 | 7500.0 | 7510.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S06 | SA | 06 | 11000.0 | 10080.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S06 | SA | 06 | 11225.0 | 10155.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S06 | SA | 06 | 11000.0 | 10210.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
EH-06 | SA | 06 | 11540 | 10600 | 0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-H06 | SA | 06 | 11450.0 | 10375.0 | 0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
RCD-R06 | RA | 06 | 12980.0 | 7700.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-R06 | RA | 06 | 12500.0 | 7425.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-R06 | RA | 06 | 11900.0 | 7700.0 | -180.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S07 | SA | 07 | 15500.0 | 7989.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S07 | SA | 07 | 15350.0 | 6792.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S07 | SA | 07 | 15500.0 | 5595.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
EH-07 | SA | 07 | 15500.0 | 4398.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-H07 | SA | 07 | 15350.0 | 4668.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
RCD-R07 | RA | 07 | 15350.0 | 4352.5 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-R07 | RA | 07 | 15525.0 | 5398.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-R07 | RA | 07 | 15350.0 | 6505.0 | 90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S09 | SA | 09 | 13200.0 | 8570.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S09 | SA | 09 | 13100.0 | 8240.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S09 | SA | 09 | 13200.0 | 7870.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S03 | SA | 03 | 17800.0 | 8600.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S03 | SA | 03 | 17650.0 | 8300.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S03 | SA | 03 | 17800.0 | 8130.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
EH-03 | SA | 03 | 17800.0 | 7740.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-H03 | SA | 03 | 17650.0 | 8010.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
VCD-S01 | SA | 01 | 16800.0 | 7581.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-S01 | SA | 01 | 16650.0 | 6468.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
FSD-S01 | SA | 01 | 16800.0 | 5355.0 | -90.0 | Proposed plan location; duct level / access envelope / OEM clearance TBC
AD-HCOM-01 | SA | COM | 1200 | 17700 | -90 | Proposed plan location; duct level / access envelope / OEM clearance TBC

## Probe_locations
tag | bubble_x_mm | bubble_y_mm | probe_x_mm | probe_y_mm | section | status
FIT-SA-01 | 1800 | 18800 | 1800 | 18800 | SA-M01 | Proposed probe attachment shown; OEM straight runs / insertion / final mounting TBC
TT-SA-01 | 800 | 17700 | 1800 | 17700 | SA-M01 | Proposed probe attachment shown; OEM straight runs / insertion / final mounting TBC
FIT-RA-01 | 3500 | 18800 | 3500 | 18800 | RA-M01 | Proposed probe attachment shown; OEM straight runs / insertion / final mounting TBC
TT-RA-01 | 4550 | 18200 | 3500 | 18200 | RA-M01 | Proposed probe attachment shown; OEM straight runs / insertion / final mounting TBC
RHT-RA-01 | 4550 | 17500 | 3500 | 17500 | RA-M01 | Proposed probe attachment shown; OEM straight runs / insertion / final mounting TBC

## Instruments
tag | parameter | location | io | basis | provision | action
TT-GF-02 | Dry bulb temperature | GF-02 Electrical panel | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-02 | Relative humidity | GF-02 Electrical panel | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-02 | Room pressure vs outdoor | GF-02 Electrical panel | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-04 | Dry bulb temperature | GF-04 Meeting | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-04 | Relative humidity | GF-04 Meeting | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-04 | Room pressure vs outdoor | GF-04 Meeting | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-04 | Heater high temperature limit | EH-04 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-08 | Dry bulb temperature | GF-08 Telecom panel | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-08 | Relative humidity | GF-08 Telecom panel | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-08 | Room pressure vs outdoor | GF-08 Telecom panel | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-05 | Dry bulb temperature | GF-05 Operator console | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-05 | Relative humidity | GF-05 Operator console | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-05 | Room pressure vs outdoor | GF-05 Operator console | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-05 | Heater high temperature limit | EH-05 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-06 | Dry bulb temperature | GF-06 Reception / corridor | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-06 | Relative humidity | GF-06 Reception / corridor | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-06 | Room pressure vs outdoor | GF-06 Reception / corridor | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Required | Monitor / alarm; final range and limits TBC
TSHH-EH-06 | Heater high temperature limit | EH-06 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-09 | Dry bulb temperature | GF-09 Toilet group: two cubicles | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-09 | Relative humidity | GF-09 Toilet group: two cubicles | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-09 | Room pressure vs outdoor | GF-09 Toilet group: two cubicles | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-GF-07 | Dry bulb temperature | GF-07 Bedroom / Resting Room | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-07 | Relative humidity | GF-07 Bedroom / Resting Room | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-07 | Room pressure vs outdoor | GF-07 Bedroom / Resting Room | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-07 | Heater high temperature limit | EH-07 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-03 | Dry bulb temperature | GF-03 Kitchen / kitchenette | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-03 | Relative humidity | GF-03 Kitchen / kitchenette | AI | 8.4.1 humidity provision | Required | Monitor / alarm; final range and limits TBC
DPT-GF-03 | Room pressure vs outdoor | GF-03 Kitchen / kitchenette | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-03 | Heater high temperature limit | EH-03 | DI | Proposed heater protection | OEM safety provision | Trip / inhibit heater; reset per OEM
TT-GF-01 | Dry bulb temperature | GF-01 Clean-agent cylinder room | AI | 8.4.1 / 15.10.1 | Required | Monitor / alarm; final range and limits TBC
RHT-GF-01 | Relative humidity | GF-01 Clean-agent cylinder room | AI | 8.4.1 humidity provision | Additional proposal | Monitor / alarm; final range and limits TBC
DPT-GF-01 | Room pressure vs outdoor | GF-01 Clean-agent cylinder room | AI | 7.13.2 / 8.4.1 minimum; added room balancing provision | Additional proposal | Monitor / alarm; final range and limits TBC
TT-SA-01 | Supply air temperature | Common supply | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
TT-RA-01 | Return air temperature | Common return | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
RHT-RA-01 | Return relative humidity | Common return | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
FIT-SA-01 | Common supply airflow | Common supply straight length per manufacturer | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
FIT-RA-01 | Common return airflow | Common return straight length per manufacturer | AI | 8.4.1 air temperature / humidity / airflow | Required | Monitor / alarm; final range and limits TBC
PDT-OA-01 | Outdoor intake filter differential pressure | F-OA-01 | AI | Additional intake filter monitoring | Additional proposal | Monitor / alarm; final range and limits TBC
PDI-OA-01 | Local intake filter differential pressure gauge | F-OA-01 | LOCAL | Additional intake filter monitoring | Additional proposal | Monitor / alarm; final range and limits TBC
TSHH-EH-COM-01 | Common heater high-limit | EH-COM-01 | DI | Proposed OEM heater safety | OEM safety provision | Trip common heater; reset per OEM
PDT-F1-A | Filter differential pressure | PAU-A filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-A | Local filter differential pressure gauge | PAU-A filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-A | Filter differential pressure | PAU-A filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-A | Local filter differential pressure gauge | PAU-A filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-A | Evaporator fan differential pressure | PAU-A fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-A | RMS vibration velocity | PAU-A frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
PDT-F1-B | Filter differential pressure | PAU-B filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-B | Local filter differential pressure gauge | PAU-B filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-B | Filter differential pressure | PAU-B filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-B | Local filter differential pressure gauge | PAU-B filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-B | Evaporator fan differential pressure | PAU-B fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-B | RMS vibration velocity | PAU-B frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
PDT-F1-C | Filter differential pressure | PAU-C filter 1 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F1-C | Local filter differential pressure gauge | PAU-C filter 1 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
PDT-F2-C | Filter differential pressure | PAU-C filter 2 | AI | 9.3.4 | Required | Dirty filter alarm; OEM threshold TBC
PDI-F2-C | Local filter differential pressure gauge | PAU-C filter 2 | LOCAL | 9.3.4 | Required | Local indication; not a PLC input
DPT-SF-C | Evaporator fan differential pressure | PAU-C fan | AI | 8.4.1 | Required | Fan proof / alarm; limit TBC
VS-PAU-C | RMS vibration velocity | PAU-C frame / fan bearing | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-03-01 | Extract fan pressure proof | EF-03-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-03-01 | RMS vibration velocity | EF-03-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-03-02 | Extract fan pressure proof | EF-03-02 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-03-02 | RMS vibration velocity | EF-03-02 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-09-01 | Extract fan pressure proof | EF-09-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-09-01 | RMS vibration velocity | EF-09-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-09-02 | Extract fan pressure proof | EF-09-02 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-09-02 | RMS vibration velocity | EF-09-02 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-EF-01-01 | Extract fan pressure proof | EF-01-01 | AI | Additional fan-proof proposal | Additional proposal | Fault changeover / alarm; final OEM proof method TBC
VS-EF-01-01 | RMS vibration velocity | EF-01-01 | AI | 8.4.1 | Required | Alarm / trip limits TBC
DPT-SF-B1-01 | Fan pressure proof | SF-B1-01 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-SF-B1-01 | RMS vibration velocity | SF-B1-01 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-SF-B1-02 | Fan pressure proof | SF-B1-02 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-SF-B1-02 | RMS vibration velocity | SF-B1-02 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-EF-B1-01 | Fan pressure proof | EF-B1-01 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-EF-B1-01 | RMS vibration velocity | EF-B1-01 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-EF-B1-02 | Fan pressure proof | EF-B1-02 | AI | Additional fan proof provision | Additional proposal | Monitor / alarm; final range and limits TBC
VS-EF-B1-02 | RMS vibration velocity | EF-B1-02 | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
TT-B1-01 | Cable basement air temperature | Cable basement | AI | 8.4.1 | Required | Monitor / alarm; final range and limits TBC
DPT-B1-01 | Basement pressure vs outdoor | Cable basement | AI | Additional coordination provision | Additional proposal | Monitor / alarm; final range and limits TBC
EM-HPCP-01 | Energy metering: V, I, kW, kWh, PF, Hz; THD for VFD | HPCP feeders >7.5 kW | COMM | 8.4.1 | Required where threshold met | Power ratings / feeder quantity / protocol TBC
AFS-EH-04 | Airflow proving switch for heater safety permissive | Electric heater EH-04 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-05 | Airflow proving switch for heater safety permissive | Electric heater EH-05 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-06 | Airflow proving switch for heater safety permissive | Electric heater EH-06 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-07 | Airflow proving switch for heater safety permissive | Electric heater EH-07 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-03 | Airflow proving switch for heater safety permissive | Electric heater EH-03 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active
AFS-EH-COM-01 | Airflow proving switch for heater safety permissive | Electric heater EH-COM-01 | DI | Explicit Rev07 OEM safety / monitoring provision; not a quoted additional TAQA minimum | Proposed; OEM proof technology / setpoint TBC | Hardwired heater inhibit on loss of airflow; status / alarm to HPCP. Independent TSHH high limit remains active

## IO_points
tag | type | signal | action | basis | status
TT-GF-02 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-02 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-02 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-04 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-04 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-04 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-04 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-08 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-08 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-08 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-05 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-05 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-05 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-05 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-06 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-06 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-06 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-06 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-09 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-09 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-09 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-GF-07 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-07 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-07 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-07 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-03 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-03 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-03 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-03 | DI | Heater high temperature limit | Trip / inhibit heater; reset per OEM | Proposed heater protection | Draft point allocation; safety integrity / module allocation TBC
TT-GF-01 | AI | Dry bulb temperature | Monitor / alarm; final range and limits TBC | 8.4.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RHT-GF-01 | AI | Relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 humidity provision | Draft point allocation; safety integrity / module allocation TBC
DPT-GF-01 | AI | Room pressure vs outdoor | Monitor / alarm; final range and limits TBC | 7.13.2 / 8.4.1 minimum; added room balancing provision | Draft point allocation; safety integrity / module allocation TBC
TT-SA-01 | AI | Supply air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
TT-RA-01 | AI | Return air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
RHT-RA-01 | AI | Return relative humidity | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
FIT-SA-01 | AI | Common supply airflow | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
FIT-RA-01 | AI | Common return airflow | Monitor / alarm; final range and limits TBC | 8.4.1 air temperature / humidity / airflow | Draft point allocation; safety integrity / module allocation TBC
PDT-OA-01 | AI | Outdoor intake filter differential pressure | Monitor / alarm; final range and limits TBC | Additional intake filter monitoring | Draft point allocation; safety integrity / module allocation TBC
TSHH-EH-COM-01 | DI | Common heater high-limit | Trip common heater; reset per OEM | Proposed OEM heater safety | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-A | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-A | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-A | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-A | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-B | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-B | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-B | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PDT-F1-C | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
PDT-F2-C | AI | Filter differential pressure | Dirty filter alarm; OEM threshold TBC | 9.3.4 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-C | AI | Evaporator fan differential pressure | Fan proof / alarm; limit TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
VS-PAU-C | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-03-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-03-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-03-02 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-03-02 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-09-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-09-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-09-02 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-09-02 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-01-01 | AI | Extract fan pressure proof | Fault changeover / alarm; final OEM proof method TBC | Additional fan-proof proposal | Draft point allocation; safety integrity / module allocation TBC
VS-EF-01-01 | AI | RMS vibration velocity | Alarm / trip limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B1-01 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-SF-B1-01 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-SF-B1-02 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-SF-B1-02 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-B1-01 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-EF-B1-01 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-EF-B1-02 | AI | Fan pressure proof | Monitor / alarm; final range and limits TBC | Additional fan proof provision | Draft point allocation; safety integrity / module allocation TBC
VS-EF-B1-02 | AI | RMS vibration velocity | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
TT-B1-01 | AI | Cable basement air temperature | Monitor / alarm; final range and limits TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
DPT-B1-01 | AI | Basement pressure vs outdoor | Monitor / alarm; final range and limits TBC | Additional coordination provision | Draft point allocation; safety integrity / module allocation TBC
EM-HPCP-01 | COMM | Energy metering: V, I, kW, kWh, PF, Hz; THD for VFD | Power ratings / feeder quantity / protocol TBC | 8.4.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-A-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-B-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
PAU-C-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-03-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-09-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-09-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-01-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
SF-B1-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-01-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-RUN | DI | Run feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-FLT | DI | Fault feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-RDY | DI | Ready feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-AUTO | DI | Auto / local selector feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-EST | DI | Local lockable E-stop feedback | Display / interlock | 7.20.4 / 8.3.1 / 15.5 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-START | DO | Start / stop command | Normal automatic operation; fire ESD inhibits | 8.2.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
EF-B1-02-SPD | AO | Speed demand | Proposed EC/VFD speed control; fan drive and ACH lower limit TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R04-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R08-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R05-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R06-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
RCD-R07-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE09-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E09-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IE03-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E03-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-E01-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-CMD | AO | Position demand | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-A-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-B-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-RA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-OA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SA-C-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-SF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-ISF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-01-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-EF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-CMD | DO | Open / close command | Pressure / standby isolation; final fail state TBC | 7.14.1 / 15.10.1 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-OPEN | DI | OPEN limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
MD-IEF-B1-02-CLOSED | DI | CLOSED limit feedback | Proof / travel fault alarm | 7.20.4 | Draft point allocation; safety integrity / module allocation TBC
EH-04-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-04-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-05-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-05-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-06-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-06-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-07-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-07-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-03-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-03-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-COM-01-ENABLE | DO | Heater enable | Only with healthy high-limit and airflow proof | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
EH-COM-01-DUTY | AO | Heating demand | Room / supply temperature control; staged or modulating OEM interface TBC | Proposed interface; confirm OEM / I&C | Draft point allocation; safety integrity / module allocation TBC
FACP-FIRE-01 | DI | Confirmed fire from FACP | Stop entire HVAC; latch fire ESD | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
HPCP-ESTOP-01 | DI | Panel emergency stop | Stop / isolate per approved ESD | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
RESET-01 | DI | Local manual reset | Only after fire signal / fault clears | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
BMS-START-01 | COMM | Initial start | Normal permissives apply | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
BMS-ESD-01 | COMM | Remote emergency stop | Stop HVAC; approved mapping TBC | 8.2.1 / 8.5.1 / 15.11.11 | Draft point allocation; safety integrity / module allocation TBC
AFS-EH-04 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-05 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-06 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-07 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-03 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending
AFS-EH-COM-01 | DI | Heater airflow proof healthy / failed | Heater enable inhibited unless airflow is proved; hardwired OEM safety circuit and PLC status | Rev07 explicit heater airflow-proof provision; confirm OEM interface | Draft allocation; OEM / I&C confirmation pending

## Cause_effect
trigger | input | equipment_action | damper_action | restart | basis
Confirmed fire | FACP -> HPCP | STOP all PAUs, extract and basement fans; heaters off | Damper fire positions per approved cause-and-effect; not inferred | Local manual reset after fire clears | 8.2.1 / 15.11.11
Normal start | HMI / BMS start + Auto | Prove duty path dampers; start chosen duty pair and duty extract fans | Standby PAU and parallel fan inlet / outlet paths isolated | Sequence / delays by approved OEM logic | 7.14 / 15.10.1
Duty PAU fault | Unit fault / fan DP | Alarm; isolate failed unit; enable available alternate | Maintain two healthy 50% units when available | Automatic fault changeover; minimum-runtime delay TBC | 7.20.3 / 15.10.1
Low / high room pressure | Room DPT | Proposed RCD / OA or extract-speed adjustment within airflow constraints | Respect cooling, fresh-air and minimum ACH limits | Alarm if targets cannot be met; revise supply / balance | 7.13.2 / 15.10.1
Extract duty fan fault | Fan fault / proof | Start standby for kitchen / toilet / basement | Prove available path; isolate failed path | CAG standby arrangement TBC | 7.19.1 / 7.18.3
Heater high limit / no flow | TSHH / AFS | Heater OFF by OEM hardwired safety; alarm / proof status to PLC | Fans / dampers per OEM sequence; fire overrides | Manual or OEM reset only after fault clears | Proposed OEM protection
Power loss / return | Mains / feeder status | HVAC stops; normal restart on restored power | Fire ESD latch overrides automatic restart | Automatic power-return restart only without fire latch | 15.11.9 / 10 / 11
Post-fire purge | Separate approved command | Not enabled by this drawing | Agent, fire fan suitability and makeup to be approved | No automatic purge assumed | C-H-SS-001 1.5; C-FF-SS-004 required

## Rev08_corrections
comment | correction | drawing | verification
Missing outside walls at connected duct joints | Use the exterior of locally joined section polygons; preserve shared external walls and remove only internal seams | D-001 to D-006 | Connected-envelope line coverage and rendered close-ups
Return branch / its dampers shown without continuous duct walls | GF-02 return header moved to x=6000; straight room branch to main at y=16400. RG-02-01/02 moved 200 mm to y=17000 for graphic / duct separation. Relocate RCD-R02, FSD-R02 and AD-R02 onto this straight | D-003 / D-004; Device_locations / Terminals | Proposed room geometry; device footprint contained in branch; route / grille coordinates registered
Instrument / component graphics not at the correct duct position | Check all branch device centres, access sides and rotation against the associated branch profile; connect off-duct temperature / humidity bubbles to their duct probes | D-004 to D-007; Device_locations / Instrument_locations | Geometric attachment checks and visual review

## Instrument_drawing_index
tag | io | location | provision | drawings
TT-GF-02 | AI | GF-02 Electrical panel | Required | 007
RHT-GF-02 | AI | GF-02 Electrical panel | Required | 007
DPT-GF-02 | AI | GF-02 Electrical panel | Additional proposal | 007
TT-GF-04 | AI | GF-04 Meeting | Required | 007
RHT-GF-04 | AI | GF-04 Meeting | Required | 007
DPT-GF-04 | AI | GF-04 Meeting | Additional proposal | 007
TSHH-EH-04 | DI | EH-04 | OEM safety provision | 014
TT-GF-08 | AI | GF-08 Telecom panel | Required | 007
RHT-GF-08 | AI | GF-08 Telecom panel | Required | 007
DPT-GF-08 | AI | GF-08 Telecom panel | Additional proposal | 007
TT-GF-05 | AI | GF-05 Operator console | Required | 007
RHT-GF-05 | AI | GF-05 Operator console | Required | 007
DPT-GF-05 | AI | GF-05 Operator console | Additional proposal | 007
TSHH-EH-05 | DI | EH-05 | OEM safety provision | 014
TT-GF-06 | AI | GF-06 Reception / corridor | Required | 007
RHT-GF-06 | AI | GF-06 Reception / corridor | Required | 007
DPT-GF-06 | AI | GF-06 Reception / corridor | Required | 007
TSHH-EH-06 | DI | EH-06 | OEM safety provision | 014
TT-GF-09 | AI | GF-09 Toilet group: two cubicles | Required | 007
RHT-GF-09 | AI | GF-09 Toilet group: two cubicles | Required | 007
DPT-GF-09 | AI | GF-09 Toilet group: two cubicles | Additional proposal | 007
TT-GF-07 | AI | GF-07 Bedroom / Resting Room | Required | 007
RHT-GF-07 | AI | GF-07 Bedroom / Resting Room | Required | 007
DPT-GF-07 | AI | GF-07 Bedroom / Resting Room | Additional proposal | 007
TSHH-EH-07 | DI | EH-07 | OEM safety provision | 014
TT-GF-03 | AI | GF-03 Kitchen / kitchenette | Required | 007
RHT-GF-03 | AI | GF-03 Kitchen / kitchenette | Required | 007
DPT-GF-03 | AI | GF-03 Kitchen / kitchenette | Additional proposal | 007
TSHH-EH-03 | DI | EH-03 | OEM safety provision | 014
TT-GF-01 | AI | GF-01 Clean-agent cylinder room | Required | 007
RHT-GF-01 | AI | GF-01 Clean-agent cylinder room | Additional proposal | 007
DPT-GF-01 | AI | GF-01 Clean-agent cylinder room | Additional proposal | 007
TT-SA-01 | AI | Common supply | Required | 007 / 008 / 012
TT-RA-01 | AI | Common return | Required | 007 / 012
RHT-RA-01 | AI | Common return | Required | 007 / 012
FIT-SA-01 | AI | Common supply straight length per manufacturer | Required | 007 / 008 / 012
FIT-RA-01 | AI | Common return straight length per manufacturer | Required | 007 / 012
PDT-OA-01 | AI | F-OA-01 | Additional proposal | 012
PDI-OA-01 | LOCAL | F-OA-01 | Additional proposal | 012
TSHH-EH-COM-01 | DI | EH-COM-01 | OEM safety provision | 014
PDT-F1-A | AI | PAU-A filter 1 | Required | 012
PDI-F1-A | LOCAL | PAU-A filter 1 | Required | 012
PDT-F2-A | AI | PAU-A filter 2 | Required | 012
PDI-F2-A | LOCAL | PAU-A filter 2 | Required | 012
DPT-SF-A | AI | PAU-A fan | Required | 012
VS-PAU-A | AI | PAU-A frame / fan bearing | Required | 012
PDT-F1-B | AI | PAU-B filter 1 | Required | 012
PDI-F1-B | LOCAL | PAU-B filter 1 | Required | 012
PDT-F2-B | AI | PAU-B filter 2 | Required | 012
PDI-F2-B | LOCAL | PAU-B filter 2 | Required | 012
DPT-SF-B | AI | PAU-B fan | Required | 012
VS-PAU-B | AI | PAU-B frame / fan bearing | Required | 012
PDT-F1-C | AI | PAU-C filter 1 | Required | 012
PDI-F1-C | LOCAL | PAU-C filter 1 | Required | 012
PDT-F2-C | AI | PAU-C filter 2 | Required | 012
PDI-F2-C | LOCAL | PAU-C filter 2 | Required | 012
DPT-SF-C | AI | PAU-C fan | Required | 012
VS-PAU-C | AI | PAU-C frame / fan bearing | Required | 012
DPT-EF-03-01 | AI | EF-03-01 | Additional proposal | 013
VS-EF-03-01 | AI | EF-03-01 | Required | 013
DPT-EF-03-02 | AI | EF-03-02 | Additional proposal | 013
VS-EF-03-02 | AI | EF-03-02 | Required | 013
DPT-EF-09-01 | AI | EF-09-01 | Additional proposal | 013
VS-EF-09-01 | AI | EF-09-01 | Required | 013
DPT-EF-09-02 | AI | EF-09-02 | Additional proposal | 013
VS-EF-09-02 | AI | EF-09-02 | Required | 013
DPT-EF-01-01 | AI | EF-01-01 | Additional proposal | 013
VS-EF-01-01 | AI | EF-01-01 | Required | 013
DPT-SF-B1-01 | AI | SF-B1-01 | Additional proposal | 013
VS-SF-B1-01 | AI | SF-B1-01 | Required | 013
DPT-SF-B1-02 | AI | SF-B1-02 | Additional proposal | 013
VS-SF-B1-02 | AI | SF-B1-02 | Required | 013
DPT-EF-B1-01 | AI | EF-B1-01 | Additional proposal | 013
VS-EF-B1-01 | AI | EF-B1-01 | Required | 013
DPT-EF-B1-02 | AI | EF-B1-02 | Additional proposal | 013
VS-EF-B1-02 | AI | EF-B1-02 | Required | 013
TT-B1-01 | AI | Cable basement | Required | 015
DPT-B1-01 | AI | Cable basement | Additional proposal | 015
EM-HPCP-01 | COMM | HPCP feeders >7.5 kW | Required where threshold met | 015
AFS-EH-04 | DI | Electric heater EH-04 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-05 | DI | Electric heater EH-05 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-06 | DI | Electric heater EH-06 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-07 | DI | Electric heater EH-07 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-03 | DI | Electric heater EH-03 | Proposed; OEM proof technology / setpoint TBC | 014
AFS-EH-COM-01 | DI | Electric heater EH-COM-01 | Proposed; OEM proof technology / setpoint TBC | 014

## Sizing_check
Section | Air | Room | Flow L/s | Width mm | Height mm | Diameter mm | Area m2 | Velocity m/s | Scheduled m/s | Difference m/s | Length m | Basis
SA-M01 | SA |  | 3697.8 | 1200 | 650 |  | 0.78 | 4.7408 | 4.7408 | -7.6923e-07 | 2.4 | Retained size / airflow; recalculated velocity only
SA-M02 | SA |  | 3033 | 1100 | 575 |  | 0.6325 | 4.7953 | 4.7953 | -3.083e-06 | 3.4 | Retained size / airflow; recalculated velocity only
SA-M03 | SA |  | 2255.3 | 950 | 500 |  | 0.475 | 4.748 | 4.748 | 0 | 5.6 | Retained size / airflow; recalculated velocity only
SA-M04 | SA |  | 1806.1 | 850 | 425 |  | 0.36125 | 4.9996 | 4.9996 | 4.7751e-06 | 3.5 | Retained size / airflow; recalculated velocity only
SA-M05 | SA |  | 921.5 | 650 | 300 |  | 0.195 | 4.7256 | 4.7256 | 1.0256e-06 | 4 | Retained size / airflow; recalculated velocity only
SA-M06 | SA |  | 503.3 | 500 | 250 |  | 0.125 | 4.0264 | 4.0264 | 0 | 2.2 | Retained size / airflow; recalculated velocity only
SA-M07 | SA |  | 457.1 | 450 | 250 |  | 0.1125 | 4.0631 | 4.0631 | 1.1111e-06 | 2.3 | Retained size / airflow; recalculated velocity only
SA-M08 | SA |  | 288.9 | 400 | 200 |  | 0.08 | 3.6113 | 3.6113 | -4.4409e-16 | 2.3 | Retained size / airflow; recalculated velocity only
SA-M09 | SA |  | 141.3 | 300 | 200 |  | 0.06 | 2.355 | 2.355 | 4.4409e-16 | 0.7 | Retained size / airflow; recalculated velocity only
RA-M01 | RA |  | 3006.6803 | 1400 | 650 |  | 0.91 | 3.304 | 3.304 | 4.3275e-06 | 2.6 | Retained size / airflow; recalculated velocity only
RA-M02 | RA |  | 2401.2169 | 1200 | 600 |  | 0.72 | 3.335 | 3.335 | 3.5389e-06 | 4.2 | Retained size / airflow; recalculated velocity only
RA-M03 | RA |  | 1682.8536 | 850 | 550 |  | 0.4675 | 3.5997 | 3.5997 | -3.2449e-06 | 4.45 | Retained size / airflow; recalculated velocity only
RA-M04 | RA |  | 1292.9902 | 800 | 450 |  | 0.36 | 3.5916 | 3.5916 | -6.4167e-07 | 3.4 | Retained size / airflow; recalculated velocity only
RA-M05 | RA |  | 467.7268 | 650 | 300 |  | 0.195 | 2.3986 | 2.3986 | -1.1333e-06 | 3.8 | Retained size / airflow; recalculated velocity only
RA-M06 | RA |  | 108.8634 | 450 | 225 |  | 0.10125 | 1.0752 | 1.0752 | 3.9753e-06 | 4.05 | Retained size / airflow; recalculated velocity only
SA-B02 | SA | 02 | 664.8 | 500 | 350 |  | 0.175 | 3.7989 | 3.7989 | -2.8571e-06 | 3 | Retained size / airflow; recalculated velocity only
SA-H02-U01 | SA | 02 | 332.4 | 500 | 350 |  | 0.175 | 1.8994 | 1.8994 | -1.4286e-06 | 1.4 | Retained size / airflow; recalculated velocity only
SA-H02-D01 | SA | 02 | 332.4 | 500 | 350 |  | 0.175 | 1.8994 | 1.8994 | -1.4286e-06 | 3.5 | Retained size / airflow; recalculated velocity only
SA-R02-01 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.1 | Retained size / airflow; recalculated velocity only
SA-R02-02 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.3 | Retained size / airflow; recalculated velocity only
SA-R02-03 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.1 | Retained size / airflow; recalculated velocity only
SA-R02-04 | SA | 02 | 166.2 | 350 |  | 350 | 0.096211 | 1.7274 | 1.7274 | -1.736e-06 | 2.3 | Retained size / airflow; recalculated velocity only
RA-B02 | RA | 02 | 605.4634 | 600 | 400 |  | 0.24 | 2.5228 | 2.5228 | 4.125e-06 | 2.5 | Retained size / airflow; recalculated velocity only
RA-H02-U01 | RA | 02 | 302.7317 | 600 | 400 |  | 0.24 | 1.2614 | 1.2614 | 2.0625e-06 | 0.6 | Retained size / airflow; recalculated velocity only
RA-H02-D01 | RA | 02 | 302.7317 | 600 | 400 |  | 0.24 | 1.2614 | 1.2614 | 2.0625e-06 | 4.5 | Retained size / airflow; recalculated velocity only
RA-R02-01 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 4.8 | Retained size / airflow; recalculated velocity only
RA-R02-02 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 1.7 | Retained size / airflow; recalculated velocity only
RA-R02-03 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 4.8 | Retained size / airflow; recalculated velocity only
RA-R02-04 | RA | 02 | 151.3658 | 300 |  | 300 | 0.070686 | 2.1414 | 2.1414 | -1.3097e-06 | 1.7 | Retained size / airflow; recalculated velocity only
SA-B04 | SA | 04 | 449.2 | 450 | 300 |  | 0.135 | 3.3274 | 3.3274 | -2.5926e-06 | 3.4 | Retained size / airflow; recalculated velocity only
SA-H04-U01 | SA | 04 | 149.7333 | 450 | 300 |  | 0.135 | 1.1091 | 1.1091 | -4.2e-06 | 0.1 | Retained size / airflow; recalculated velocity only
SA-H04-D01 | SA | 04 | 299.4667 | 450 | 300 |  | 0.135 | 2.2183 | 2.2183 | 1.6074e-06 | 2.2 | Retained size / airflow; recalculated velocity only
SA-H04-D02 | SA | 04 | 149.7333 | 450 | 300 |  | 0.135 | 1.1091 | 1.1091 | -4.2e-06 | 2.4 | Retained size / airflow; recalculated velocity only
SA-R04-01 | SA | 04 | 149.7333 | 325 |  | 325 | 0.082958 | 1.8049 | 1.8049 | -3.6616e-06 | 1.1 | Retained size / airflow; recalculated velocity only
SA-R04-02 | SA | 04 | 149.7333 | 325 |  | 325 | 0.082958 | 1.8049 | 1.8049 | -3.6616e-06 | 1.4 | Retained size / airflow; recalculated velocity only
SA-R04-03 | SA | 04 | 149.7333 | 325 |  | 325 | 0.082958 | 1.8049 | 1.8049 | -3.6616e-06 | 1 | Retained size / airflow; recalculated velocity only
RA-B04 | RA | 04 | 389.8634 | 500 | 350 |  | 0.175 | 2.2278 | 2.2278 | 8e-07 | 2.55 | Retained size / airflow; recalculated velocity only
RA-H04-U01 | RA | 04 | 129.9545 | 500 | 350 |  | 0.175 | 0.7426 | 0.7426 | -3.0686e-06 | 0.1 | Retained size / airflow; recalculated velocity only
RA-H04-D01 | RA | 04 | 259.9089 | 500 | 350 |  | 0.175 | 1.4852 | 1.4852 | 3.8629e-06 | 2.6 | Retained size / airflow; recalculated velocity only
RA-H04-D02 | RA | 04 | 129.9545 | 500 | 350 |  | 0.175 | 0.7426 | 0.7426 | -3.0686e-06 | 3.3 | Retained size / airflow; recalculated velocity only
RA-R04-01 | RA | 04 | 129.9545 | 300 |  | 300 | 0.070686 | 1.8385 | 1.8385 | -4.2993e-07 | 2.3 | Retained size / airflow; recalculated velocity only
RA-R04-02 | RA | 04 | 129.9545 | 300 |  | 300 | 0.070686 | 1.8385 | 1.8385 | -4.2993e-07 | 1.9 | Retained size / airflow; recalculated velocity only
RA-R04-03 | RA | 04 | 129.9545 | 300 |  | 300 | 0.070686 | 1.8385 | 1.8385 | -4.2993e-07 | 2.3 | Retained size / airflow; recalculated velocity only
SA-B08 | SA | 08 | 884.6 | 600 | 400 |  | 0.24 | 3.6858 | 3.6858 | 3.3333e-06 | 4.5 | Retained size / airflow; recalculated velocity only
SA-H08-U01 | SA | 08 | 294.8667 | 600 | 400 |  | 0.24 | 1.2286 | 1.2286 | 1.1125e-06 | 0.2 | Retained size / airflow; recalculated velocity only
SA-H08-D01 | SA | 08 | 589.7333 | 600 | 400 |  | 0.24 | 2.4572 | 2.4572 | 2.2208e-06 | 2.1 | Retained size / airflow; recalculated velocity only
SA-H08-D02 | SA | 08 | 294.8667 | 600 | 400 |  | 0.24 | 1.2286 | 1.2286 | 1.1125e-06 | 2.5 | Retained size / airflow; recalculated velocity only
SA-R08-01 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2 | Retained size / airflow; recalculated velocity only
SA-R08-02 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2.1 | Retained size / airflow; recalculated velocity only
SA-R08-03 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2 | Retained size / airflow; recalculated velocity only
SA-R08-04 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2.1 | Retained size / airflow; recalculated velocity only
SA-R08-05 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2 | Retained size / airflow; recalculated velocity only
SA-R08-06 | SA | 08 | 147.4333 | 325 |  | 325 | 0.082958 | 1.7772 | 1.7772 | 1.3589e-06 | 2.1 | Retained size / airflow; recalculated velocity only
RA-B08 | RA | 08 | 825.2634 | 700 | 450 |  | 0.315 | 2.6199 | 2.6199 | 3.7778e-06 | 2.85 | Retained size / airflow; recalculated velocity only
RA-H08-U01 | RA | 08 | 275.0878 | 700 | 450 |  | 0.315 | 0.87329 | 0.87329 | 4.5937e-06 | 0.2 | Retained size / airflow; recalculated velocity only
RA-H08-D01 | RA | 08 | 550.1756 | 700 | 450 |  | 0.315 | 1.7466 | 1.7466 | -8.1587e-07 | 2.3 | Retained size / airflow; recalculated velocity only
RA-H08-D02 | RA | 08 | 275.0878 | 700 | 450 |  | 0.315 | 0.87329 | 0.87329 | 4.5937e-06 | 3.7 | Retained size / airflow; recalculated velocity only
RA-R08-01 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 3 | Retained size / airflow; recalculated velocity only
RA-R08-02 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 2.3 | Retained size / airflow; recalculated velocity only
RA-R08-03 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 3 | Retained size / airflow; recalculated velocity only
RA-R08-04 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 2.3 | Retained size / airflow; recalculated velocity only
RA-R08-05 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 3 | Retained size / airflow; recalculated velocity only
RA-R08-06 | RA | 08 | 137.5439 | 300 |  | 300 | 0.070686 | 1.9458 | 1.9459 | -1.8881e-06 | 2.3 | Retained size / airflow; recalculated velocity only
SA-B05 | SA | 05 | 777.7 | 600 | 350 |  | 0.21 | 3.7033 | 3.7033 | 3.3333e-06 | 12.2 | Retained size / airflow; recalculated velocity only
SA-H05-U01 | SA | 05 | 777.7 | 600 | 350 |  | 0.21 | 3.7033 | 3.7033 | 3.3333e-06 | 0.4 | Retained size / airflow; recalculated velocity only
SA-H05-U02 | SA | 05 | 466.62 | 600 | 350 |  | 0.21 | 2.222 | 2.222 | 0 | 2.2 | Retained size / airflow; recalculated velocity only
SA-H05-U03 | SA | 05 | 311.08 | 600 | 350 |  | 0.21 | 1.4813 | 1.4813 | 3.3333e-06 | 2.3 | Retained size / airflow; recalculated velocity only
SA-R05-01 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 3.1 | Retained size / airflow; recalculated velocity only
SA-R05-02 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 2.6 | Retained size / airflow; recalculated velocity only
SA-R05-03 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 4.3 | Retained size / airflow; recalculated velocity only
SA-R05-04 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 3.1 | Retained size / airflow; recalculated velocity only
SA-R05-05 | SA | 05 | 155.54 | 325 |  | 325 | 0.082958 | 1.8749 | 1.8749 | 1.8702e-06 | 2.6 | Retained size / airflow; recalculated velocity only
RA-B05 | RA | 05 | 718.3634 | 650 | 400 |  | 0.26 | 2.7629 | 2.7629 | -3.8846e-06 | 11.4 | Retained size / airflow; recalculated velocity only
RA-H05-U01 | RA | 05 | 574.6907 | 650 | 400 |  | 0.26 | 2.2103 | 2.2104 | -1.1077e-06 | 0.3 | Retained size / airflow; recalculated velocity only
RA-H05-U02 | RA | 05 | 431.018 | 650 | 400 |  | 0.26 | 1.6578 | 1.6578 | 1.6692e-06 | 2.1 | Retained size / airflow; recalculated velocity only
RA-H05-U03 | RA | 05 | 287.3454 | 650 | 400 |  | 0.26 | 1.1052 | 1.1052 | 4.4462e-06 | 4.2 | Retained size / airflow; recalculated velocity only
RA-H05-D01 | RA | 05 | 143.6727 | 650 | 400 |  | 0.26 | 0.55259 | 0.55259 | -2.7769e-06 | 1.5 | Retained size / airflow; recalculated velocity only
RA-R05-01 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 5.2 | Retained size / airflow; recalculated velocity only
RA-R05-02 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 4.1 | Retained size / airflow; recalculated velocity only
RA-R05-03 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 5.2 | Retained size / airflow; recalculated velocity only
RA-R05-04 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 4.1 | Retained size / airflow; recalculated velocity only
RA-R05-05 | RA | 05 | 143.6727 | 300 |  | 300 | 0.070686 | 2.0326 | 2.0326 | 2.6125e-06 | 0.2 | Retained size / airflow; recalculated velocity only
SA-B06 | SA | 06 | 418.2 | 450 | 300 |  | 0.135 | 3.0978 | 3.0978 | -2.2222e-06 | 2.1 | Retained size / airflow; recalculated velocity only
SA-H06-D01 | SA | 06 | 139.4 | 450 | 300 |  | 0.135 | 1.0326 | 1.0326 | 2.5926e-06 | 4.6 | Retained size / airflow; recalculated velocity only
SA-R06-01 | SA | 06 | 139.4 | 300 |  | 300 | 0.070686 | 1.9721 | 1.9721 | -3.4163e-06 | 7.2 | Retained size / airflow; recalculated velocity only
SA-R06-02 | SA | 06 | 139.4 | 300 |  | 300 | 0.070686 | 1.9721 | 1.9721 | -3.4163e-06 | 3.7 | Retained size / airflow; recalculated velocity only
SA-R06-03 | SA | 06 | 139.4 | 300 |  | 300 | 0.070686 | 1.9721 | 1.9721 | -3.4163e-06 | 4.5 | Retained size / airflow; recalculated velocity only
RA-B06 | RA | 06 | 358.8634 | 550 | 350 |  | 0.1925 | 1.8642 | 1.8642 | -4.5974e-06 | 6.05 | Retained size / airflow; recalculated velocity only
RA-H06-D01 | RA | 06 | 89.7158 | 550 | 350 |  | 0.1925 | 0.46606 | 0.46606 | -3.6519e-06 | 4.6 | Retained size / airflow; recalculated velocity only
RA-R06-01 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 11.55 | Retained size / airflow; recalculated velocity only
RA-R06-02 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 4.95 | Retained size / airflow; recalculated velocity only
RA-R06-03 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 5.85 | Retained size / airflow; recalculated velocity only
RA-R06-04 | RA | 06 | 89.7158 | 300 |  | 300 | 0.070686 | 1.2692 | 1.2692 | -3.9789e-07 | 2.1 | Retained size / airflow; recalculated velocity only
SA-B09 | SA | 09 | 46.2 | 200 | 150 |  | 0.03 | 1.54 | 1.54 | 2.2204e-16 | 2.4 | Retained size / airflow; recalculated velocity only
SA-H09-D01 | SA | 09 | 46.2 | 200 | 150 |  | 0.03 | 1.54 | 1.54 | 2.2204e-16 | 0.1 | Retained size / airflow; recalculated velocity only
SA-H09-D02 | SA | 09 | 23.1 | 200 | 150 |  | 0.03 | 0.77 | 0.77 | 1.1102e-16 | 1.8 | Retained size / airflow; recalculated velocity only
SA-R09-01 | SA | 09 | 23.1 | 150 |  | 150 | 0.017671 | 1.3072 | 1.3072 | 2.5993e-06 | 0.2 | Retained size / airflow; recalculated velocity only
SA-R09-02 | SA | 09 | 23.1 | 150 |  | 150 | 0.017671 | 1.3072 | 1.3072 | 2.5993e-06 | 0.2 | Retained size / airflow; recalculated velocity only
SA-B07 | SA | 07 | 168.2 | 300 | 250 |  | 0.075 | 2.2427 | 2.2427 | -3.3333e-06 | 7.1 | Retained size / airflow; recalculated velocity only
SA-H07-D01 | SA | 07 | 168.2 | 300 | 250 |  | 0.075 | 2.2427 | 2.2427 | -3.3333e-06 | 0.4 | Retained size / airflow; recalculated velocity only
SA-R07-01 | SA | 07 | 168.2 | 350 |  | 350 | 0.096211 | 1.7482 | 1.7482 | -4.1516e-06 | 0.2 | Retained size / airflow; recalculated velocity only
RA-B07 | RA | 07 | 108.8634 | 350 | 250 |  | 0.0875 | 1.2442 | 1.2442 | 3.0286e-06 | 6.5 | Retained size / airflow; recalculated velocity only
RA-H07-D01 | RA | 07 | 108.8634 | 350 | 250 |  | 0.0875 | 1.2442 | 1.2442 | 3.0286e-06 | 0.8 | Retained size / airflow; recalculated velocity only
RA-R07-01 | RA | 07 | 108.8634 | 300 |  | 300 | 0.070686 | 1.5401 | 1.5401 | 1.9236e-06 | 0.6 | Retained size / airflow; recalculated velocity only
SA-B03 | SA | 03 | 147.6 | 300 | 200 |  | 0.06 | 2.46 | 2.46 | 0 | 2.4 | Retained size / airflow; recalculated velocity only
SA-H03-D01 | SA | 03 | 147.6 | 300 | 200 |  | 0.06 | 2.46 | 2.46 | 0 | 0.7 | Retained size / airflow; recalculated velocity only
SA-R03-01 | SA | 03 | 147.6 | 325 |  | 325 | 0.082958 | 1.7792 | 1.7792 | 4.1944e-07 | 0.4 | Retained size / airflow; recalculated velocity only
SA-B01 | SA | 01 | 141.3 | 300 | 200 |  | 0.06 | 2.355 | 2.355 | 4.4409e-16 | 7.5 | Retained size / airflow; recalculated velocity only
SA-H01-D01 | SA | 01 | 141.3 | 300 | 200 |  | 0.06 | 2.355 | 2.355 | 4.4409e-16 | 0.3 | Retained size / airflow; recalculated velocity only
SA-R01-01 | SA | 01 | 141.3 | 300 |  | 300 | 0.070686 | 1.999 | 1.999 | -3.9148e-06 | 1.3 | Retained size / airflow; recalculated velocity only
EA-B09 | EA | 09 | 64.8889 | 250 | 200 |  | 0.05 | 1.2978 | 1.2978 | -2.22e-06 | 6.7 | Retained size / airflow; recalculated velocity only
EA-R09-01 | EA | 09 | 32.4444 | 150 |  | 150 | 0.017671 | 1.836 | 1.836 | -3.9656e-08 | 0.5 | Retained size / airflow; recalculated velocity only
EA-R09-02 | EA | 09 | 32.4444 | 150 |  | 150 | 0.017671 | 1.836 | 1.836 | -3.9656e-08 | 2.3 | Retained size / airflow; recalculated velocity only
EA-B03 | EA | 03 | 147.6 | 300 | 200 |  | 0.06 | 2.46 | 2.46 | 0 | 1.9 | Retained size / airflow; recalculated velocity only

## Comment_closure
Comment | Rev08 action | Drawing / register | Status
Outside walls missing at connected joints | Preserved the outside envelope of the connected duct profiles; removed internal seams only | D-001 to D-006; geometry validation | Corrected; four marked-junction checks passed
GF-02 return branch crossed its own header | Moved header to x=6000 mm and made branch straight at y=16400 mm; two upper grilles moved +200 mm | D-003 / D-004; Duct_sections / Terminals | Proposed positions registered; levels and ceiling coordination pending
Branch dampers / heaters outside duct straight | Repositioned branch devices and verified each core footprint within its associated duct; AD centres on duct wall | D-004 to D-006; Device_locations | Drawing geometry checked; OEM access envelopes pending
Duct sensor tags lacked measurement connections | Added probe leaders and common-duct context; verified five measurement points inside their assigned main ducts | D-007; Probe_locations | Proposed probe attachment checked; OEM mounting pending
Device tags overlapped duct symbols | Placed tags according to duct orientation and separated access-door leaders | D-004 to D-006 | Revised enlarged views visually checked
Earlier transition / access / heater proof provisions | Retained 13 main tapers, 15 room boots, 49 external adaptors, 21 AD tags and six AFS-EH inputs from Rev07 | D-008 / D-009 / D-011 / D-012; Transitions / IO_points | Retained; no new airflow or I/O allocation in Rev08